ADDRESSABLE FIRE ALARM SYSTEM – SECTION 283111

TABLE OF CONTENTS

ADDRESSABLE FIRE ALARM SYSTEMS - SECTION 283111	1

PART 1 - GENERAL	1

1.01	RELATED DOCUMENTS:	1

1.02	SUMMARY	1

1.03	ALLOWANCES	2

1.04	UNIT PRICES	2

1.05	DEFINITIONS	2

1.06	SYSTEM DESCRIPTION	2

1.07	PERFORMANCE REQUIREMENTS	3

1.08	SUBMITTALS	7

1.09	QUALITY ASSURANCE	11

1.10	DELIVERY STORAGE AND HANDLING	13

1.11	PROJECT CONDITIONS	13

1.12	COORDINATION	13

1.13	WARRANTY:	13

1.14	SERVICE AGREEMENT	13

1.15	EXTRA MATERIALS	13

PART 2 - PRODUCTS	14

2.01	MANUFACTURERS	14

2.02	FIRE ALARM CONTROL PANEL (FACP):	15

2.03	FIRE DETECTORS	17

2.04	AIR SAMPLING SMOKE DETECTOR:	18

2.05	MANUAL PULL STATIONS:	21

2.06	NOTIFICATION APPLIANCES	21

2.07	AMPLIFIERS, PREAMPLIFIERS, TONE GENERATORS:	22

2.08	[ELECTROMAGNETIC DOOR HOLDERS:	22

2.09	[REMOTE PANELS:	23

2.10	[GRAPHIC ANNUNCIATOR	23

2.11	SYSTEM PRINTER	23

2.12	REMOTE MONITORING SYSTEM:	24

2.13	POWER SUPPLIES	24

2.14	LOAD CONTROL RELAYS:	24

2.15	INTERFACE MODULES:	24

2.16	[FIREFIGHTER TELEPHONE COMMUNICATION SYSTEM	25

PART 3 - EXECUTION	25

3.01	PRIMARY POWER:	25

3.02	SYSTEM FIELD WIRING AND CONDUIT	26

3.03	FIRESTOPPING:	27

3.04	MARKING:	27

3.05	DEVICE INSTALLATION:	27

3.06	TESTS	29

3.07	TRAINING	30

3.08	KEYS	31

EDITING NOTE

All bracketed blanks, words, phrases, sentences, and paragraphs in this specification require the editor to either include or delete the bracketed section, or provide required information.

# ADDRESSABLE FIRE ALARM SYSTEMS - SECTION 283111

GENERAL

RELATED DOCUMENTS:

Drawings and General Provision of Contract, including General and Special Conditions and Division 1 Specification Section, apply to work of this Section.

Related Sections:

General and Special conditions

Division 1:  Submittals

Division 7:  Firestopping

Division 8:  Door Release and unlocking

Division 9:  Painting

Division 14:  Elevators

Division 21:  Sprinkler System, Fire Pumps

Division 23:

Air Handling Systems

Smoke Management Systems

Stair Pressurization Systems

Gaseous suppression systems

Division 26: Basic Electrical Requirements

SUMMARY

Scope:  This work includes designing and providing a new, complete, addressable fire alarm system as described herein and on the contract drawings for <Building Name>. The system shall include all wiring, raceways, pull boxes, terminal cabinets, outlet and mounting boxes, control equipment, alarm and supervisory signals, initiating devices, alarm notification appliances, interfaced equipment, and all other accessories and miscellaneous items required for a complete operating system even though each item is not specifically mentioned or described.

Existing Equipment:  Existing fire alarm equipment shall be maintained fully operational until the new equipment has been tested and accepted by the Smithsonian Institution.  As new equipment is installed, it shall be labeled "NOT IN SERVICE" until the new equipment is accepted.  Once the new system is installed, tested, and accepted by the Smithsonian, the labels on the new equipment shall be removed and the existing equipment shall be labeled "NOT IN SERVICE" until removed from the building.  Just prior to demolition and construction activities (dust producing activities), dust covers should be installed over spot type smoke detectors and the duct detector for the air handling unit serving the area.  The dust covers are to be removed at the end of the work day.

Equipment Removal:  After acceptance of the new system by the Smithsonian, all existing equipment not connected to the new system shall be removed and all damaged surfaces shall be restored to finishes similar to surrounding walls/ceiling/floor.  Smoke detectors shall remain covered during removal and while in storage.   Operational equipment which was removed shall be carefully packaged, labeled, and turned over to the COTR.  Other material, such as conduit and electrical boxes, shall be removed from the site and disposed of by the Contractor.

Repair/Service Replacement Parts:  Repair services and replacement parts for the system shall be furnished under this contract after the date of final acceptance of work by the Smithsonian Institution.  On-site service during the warranty period shall be provided within 24 hours after notification.  All repairs shall be completed within 48 hours after notification.

ALLOWANCES

[List Allowances, if included as part of the contract. Confirm with OSHEM and COTR]

UNIT PRICES

[List Unit Prices, if included as part of the contract. Confirm with OSHEM and COTR]

DEFINITIONS

COTR: Contracting Officer Technical Representative

FM: FM Global (Factory Mutual)

FPE: Fire Protection Engineer

Furnish: To supply the stated equipment or materials

Install: To set in position and connect or adjust for use

NFPA: National Fire Protection Association

NICET: National Institute for Certification in Engineering Technologies

OSHEM: Office of Safety Health and Environmental Management

Provide: To furnish and install the stated equipment or materials

UL: Underwriters Laboratories

SYSTEM DESCRIPTION

The System shall be a complete, supervised, noncoded, addressable multiplex fire alarm system with voice/strobe evacuation, intelligent analog alarm initiation, conventional smoke detection initiation, and complying with all aspects of the applicable documents listed herein.

PERFORMANCE REQUIREMENTS

Comply with NFPA 72 and all contract documents and specification requirements.

The system shall be classified as a proprietary protective signaling system.

Control features:

The system fire alarm control panel shall be tied-to the central monitoring system. The Keltron monitoring system uses the existing SI network to communicate fire alarm conditions. A compatible fire alarm system, the appropriate Keltron LS Net transceiver and associated network connections must be installed. The final connections and programming will be performed by SI staff.

[The system fire alarm control panel shall be tied to a remote panel and a graphic annunciator in the locations identified on the drawings.]

Any intelligent analog smoke detector or conventional smoke detector zone shall include a selectable alarm confirmation capability.  Alarm conditions on these devices are processed through a confirmation period of 45 seconds.  Over the next 300 seconds, a signal justification period is initiated where any subsequent alarms are reported immediately.

A subprogram shall be provided to allow environmental compensating for smoke detector sensitivity.  Each smoke detector shall be programmed with this capability.

The system shall provide a field test function where one person can test the complete system or a specified area at the fire alarm control panel while maintaining full operational function of other areas not under test.  Alarms, troubles, device types, and the initiation device addresses shall be logged to the system printer and historical memory.

Provide a manual pull station attached to the fire alarm control panel that activates the general alarm.  Resetting the manual pull station (and all other activated alarms) will cause the general alarm to cease operating.  OSHEM must approve the final sequence of operation.

Provide program capability via switches or buttons in a locked portion of the fire alarm control panel to bypass the notification appliance circuits, air handler shutdown, smoke control operation, elevator recall, fire door release, and door unlocking features.  Operation of these switches or buttons shall indicate this action as a supervisory signal on the FACP display and printer output.

History Logging - recirculating last 500 events, minimum.  History shall be downloadable by classification for selective event reports.

Supervision

Style B initiating device circuits.

Style 4 signaling line circuits for each floor.

Style 7 signaling line circuits for the network.

Class B notification appliance circuits.

Provide electrical supervision of the primary power (AC) supply, presence of the battery, battery voltage, and placement of system modules within the control panel.

Provide electrical supervision of the circuits leading to interfacing modules for the monitoring of contact type initiation devices, the control of electrical devices, fire pump controllers, load control relays (controlling elevators and HVAC equipment), and each independent smoke detection, kitchen, and gaseous fire suppression systems.

Spare capacity:

All installed signaling line circuits and notification appliance circuits shall have 20 percent spare capacity.

All amplifiers shall have 20 percent spare capacity.

Battery size shall be a minimum of 125% of the calculated requirement.

Alarm Functions: Fire alarm system functions and operations shall be as indicated on the Alarm Function Matrix included at the end of this part.  Operation of an alarm initiating device shall cause the functions indicated on the matrix to occur as described below:

Sound General Evacuation Alarm: This function shall cause all strobe lights to activate and speakers in the building to sound a slow whoop for 3 cycles followed by the voice message,

"May I have your attention please!  May I have your attention please!  A fire has been reported in the building.  Please walk to the nearest exit and leave the building.  Do not use the elevators."

This is repeated until the control panel is reset.  After the digital message has ended, or if the digitally prerecorded message shall fail for any reason, the alarm signal shall revert back to a slow whoop which will continue until manually silenced.  It shall also be possible to preempt the whoop signal or prerecorded voice evacuation message and sound a live message from the microphone at the Fire alarm Master CPU location on a floor by floor basis.  All floors not selected for a manual message shall continue to receive the pre-recorded message or whoop signal.

Initiate Pre-signal Alarm: This function shall cause an audible and visual alarm and indication to be provided at the FACP.  Activation of an initiation device will be annunciated at the FACP only, without activation of the General Evacuation Alarm.

Release Held-Open Fire Doors: This function shall cause all fire doors in the building which are held open by electrical hold-open/release mechanisms to be released, and allowed to close.

Unlock Time Delay Hardware on Exit Doors: This function shall cause a signal to be sent to all exit doors provided with electrically operated locks to become unlocked and free for egress.

Shutdown Supply Fan Served: This function shall cause the air handling system supply fan to shut down.

Initiate Smoke Management Sequence of Operation: The building HVAC system [Smoke Removal System] is arranged to exhaust smoke from a fire area.  The sequence of operation is described in Division 23.  The fire alarm system shall provide any and all such interfaces/control points as required to properly activate smoke management systems.  Only the first fire alarm system initiating device to go into alarm condition will activate the smoke control functions.  Any subsequent devices will have no effect on the smoke control mode.  The exact quantities and locations of all such interface points shall be coordinated with the automatic control systems supplier.

Close Smoke Damper: This function shall cause smoke dampers installed in HVAC systems to shut-down.

Initiate Stairwell Pressurization: This function shall initiate the stairwell pressurization systems in each building stairwell.  Each stairwell has a separate pressurization system which will be independently activated.  The full extent and requirements of this system are described under Division 23.  The fire alarm system shall provide any and all such interfaces/control points as required to properly activate this smoke management system.

Initiate Elevator Recall: This function shall cause a signal to be sent to the elevator controller recalling the elevator to the preselected floor, or if the activated initiation device is on the preselected floor, the elevator will be recalled to the preselected secondary floor.  Recall shall be initiated for all elevators served by a common shaft, elevator machine room, or elevator lobby.

Shutdown Power to Elevator Equipment: This function shall cause a signal to be sent to a shunt trip switch in the power circuit serving the elevator to cause elevator shutdown.  This shall be typical for all elevators served by a common shaft, elevator machine room or elevator lobby.

Activate Fire Suppression System Served:  This function shall cause a signal to be sent to an interface device to operate a solenoid and activate a fire suppression system.

Shutdown Exhibit Hall Audio/Visual Equipment:    This function shall cause a signal to be sent to a circuit shunt trip causing audio/visual equipment to shut down.

Illuminate LED on Device in Alarm: This function shall cause an LED, integral to a device, to illuminate, indicating that the device is in alarm.  For contact devices, such as sprinkler valve tamper switches, the LED shall be built into the intelligent system interface module monitoring the device.

Activate audio/visual signals and display address on the FACP: This function shall illuminate an alarm indicating LED, sound an audible alarm, and display a device address at the FACP when the system is in an alarm condition. [Signals shall also be transmitted to a computer control display system.]

[Transmit Event to Central Monitoring Station: This function shall cause the event to be transmitted to the central monitoring station at the Smithsonian Institution SIPPS Control Center.  The message sent shall include the building of origin and the identical message displayed on the fire alarm control panel LCD display board.]

Print Address, Date, Time, and Type of Alarm: This function shall cause the fire alarm system printer to print a message identical to that shown on the FACP LCD display board.

Activate Audio/Visual Signals and Address Display on Remote Panel or Graphic Annunciator Panel:  This function shall cause the event to be transmitted to a remote panel, whose location is shown on the drawings.  The message sent shall be the same message displayed on the FACP LCD display board.

Signal Confirmation:  This function shall cause the fire alarm control panel to reset the activated device and wait for a second alarm activation.  Alarm conditions are processed through a confirmation period of 45 seconds.  Over the next 300 seconds, a signal justification period is initiated where any subsequent alarms are reported immediately.

Trouble Functions:  Provide the following actions and indications at the FACP upon a single break, open condition, or ground fault on all supervised circuits which may prevent the required operation of the system:

Annunciate at the FACP: A yellow visual signal, audible alarm, and alphanumeric LCD display of type of trouble, and device address.

The fire alarm system printer shall print a message identical to that shown on the LCD display on the FACP.  In addition, the printed hard copy of the event shall indicate the date and time at which it occurred.

Send a signal to the existing central monitoring system.  This message shall include the building of origin as well as all information indicated to be displayed on the FACP.

Send a signal to the remote panel shown on the drawings.  This message shall include the building of origin as well as all information indicated to be displayed on the FACP.   The message sent shall be the same message displayed on the FACP LCD display board.

Fire suppression system control valves shall be supervised to ensure circuit integrity and open position.  Closing a control valve shall cause a trouble condition.

Each independent fire detection, kitchen, and fire suppression system shall be monitored for trouble conditions.  Each monitored condition shall be provided with a separate address.

Fire Alarm Signal Initiation Shall Be By One Or More Of The Following Devices:

Manual pull station

Heat detector

Addressable area smoke detector

Projected beam detector

Aspiration Smoke Detector Alarm

Automatic sprinkler system water flow switch.

Combustible Gas Detection System

Conventional initiation device zone (for legacy systems).

Flame detector

[Operation of the building fire pump or pump running signal].

Supervisory signal initiation shall be by one or more of the following devices or actions:

Operation of a fire-protection system valve tamper switch.

[Operation of the building fire pump] and/or any associated fire pump system troubles/ supervisory signals.

Duct smoke detector

Laser Scanner Aspiration Smoke Detector Alert

Operation of any non-fire system alarms as designated on the Matrix.

[Generator running]

Generator fault

Fire pump fault

System trouble signal initiation shall be by one or more of the following devices or actions:

Loss of primary power at the FACP.

Ground or a single break in FACP internal circuits.

Abnormal ac voltage at the FACP.

A break in standby battery circuitry.

Open circuits, shorts and grounds of wiring for initiating device, signaling line, and notification-appliance circuits.

Failure of battery charging.

Abnormal position of any switch at the FACP or annunciator.

Amplifier failure

Opening, tampering, or removal of alarm-initiating and supervisory signal-initiating devices.

SUBMITTALS

General:	Refer to Section "SUBMITTALS" for basic information relating to submittal requirements.  Submit 6 complete sets of submittals.  Partial submittals will not be acceptable and will be returned without review.  Before any work is commenced, the submittal must be approved by the Office of Safety, Health and Environmental Management (OSHEM). Any work performed by the contractor prior to their approval will be at the contractor’s own risk. If such work is contrary to applicable codes and contract documents, the contractor shall bear all costs including, but not limited to, demolition, reconstruction, and all costs and expenses associated with revising the fire alarm system to meet all applicable codes and contract document requirements.

System Description:  Submit a detailed description of the control panel as it shall operate for this specific installation.  General system descriptions from the catalog cuts and copies of the Systems Design Operation portion of this specification will not be acceptable.

Equipment:  Include annotated catalog data showing manufacturer's name, model, voltage, and catalog numbers for all equipment and components of the following:

Fire Alarm Control Panel (FACP) (Including Printers, interface modules, Covers, Console Rack, Video Display Unit, amplifier panels etc.)

Strobe Power Extender Panels

Storage Batteries

Battery Charger

Cabinet

Manual Pull Station

Addressable Interface Devices

Terminal Cabinets/Assemblies

Addressable Relays And Interface Modules

Graphic Annunciator Panel

Annunciation devices (speakers, strobes, bells, etc.)

Fire Detector (smoke, heat, flame, etc.)

Amplifiers

Tone Generators

Digitalized Voice Generators

Firefighter Telephones

Waterflow Switch

Tamper Switch

Electromagnetic Door Holder

Remote Fire Alarm Control Unit

Wire

Boxes

Terminal strips

Relays

Transient Voltage Surge Suppressors

Conduit

Support

Shop Drawings:  Provide 5 sets of working drawings and 1 set of reproducible mylar sepia on sheets not smaller than 24 inches by 36 inches (609 mm by 914 mm).  Shop drawings shall be prepared on a computer Aided Drafting (CAD) System. As a minimum, the shop drawing submittal shall include the following:

Interior wiring diagram for FACP.

Provide point-to-point wiring diagrams on floor plans at a scale of not less than 1/8” = 1’-0” (1:100), showing all field devices (indicating and initiating devices, relays, switches, etc), field interconnections, the routing of conduit and circuits between devices, electrical boxes, terminal cabinets, risers, and the FACP. All device circuit numbers and addresses shall be indicated.

Field wiring color code scheme.

Locations for all ceiling mounted equipment shall be coordinated with lighting fixtures, air outlets, ductwork and other fixtures.  All detectors shall be centered and aligned with ceiling tiles and/or other ceiling mounted devices.

Provide complete riser diagrams indicating the wiring sequence of all devices and their connections to the control equipment.  Provide a color code schedule for the wiring.  Provide floor plans showing the location of all devices and equipment.

Provide detailed drawings of the graphic annunciator.

Detailed sequence of operations and matrix.

As-Built (Record) Working Drawings:  On a daily basis the contractor's superintendent shall record as-built conditions on a set of Shop Drawings maintained at the job site.  Two sets of Shop Drawings reflecting as-built conditions shall be available prior to and for use in the final acceptance test.  Two weeks after the acceptance test and before final acceptance of the work, furnish four complete sets of as-built drawings.  The drawings shall be prepared on uniform sized sheets not less than 24 inches by 36 inches (609 mm by 914 mm).   The drawings shall include:

As-built location of all devices and equipment.  Device addresses shall be listed next to each device

Complete wiring diagrams showing connections between all devices and equipment.  Each conductor shall be numbered at every junction point with indication of origination and termination points.

Riser diagram

All deviations from the project drawings and approved shop drawings

Record Drawing Software: Provide three (3) compact discs containing CAD based drawings in DXF format of all as-built drawings and schematics.

Device Addresses: Prior to fire system installation provide for approval a complete list of device addresses with corresponding commands, controls, and sequence of operation.

Qualification Data:  For Designer and Installer.

Strobe and Voice Evacuation Circuit Labels:  Prior to fire system installation provide for approval a complete list of area descriptions for strobe and voice evacuation circuits to be labeled on the fire alarm panel.

Descriptions on Graphic Annunciators:  Prior to fire system installation, provide descriptive labels for graphic annunciator labeling which will include strobe and voice evacuation zones, sprinkler zones, sprinkler valve locations, HVAC zones, fire walls, stairwells, and elevators.

Service Manuals and Equipment Descriptions : Thirty days prior to the final acceptance test and after the preliminary testing has been completed submit the following:

Furnish four (4) bound copies of complete service manuals to include: device and board specifications, operation, installation, and maintenance manual; manufacturers installation instructions for all aspects of the installation; Walktest Operating Instructions;  manufacturers wiring specifications for the system; training manual.

Maintenance checklists for equipment.

As-built circuit diagrams, complete with color-code scheme, and device descriptions.

Complete parts list by make model number and manufacturer.

List of smoke detector addresses and corresponding sensitivity readings.

Copies of approved submittal materials.

Calculations: Submit substantiating battery calculations for supervisory and alarm power requirements.  Ampere-hour requirements for each system component and each panel component shall be submitted with the calculations.  Calculations shall include:

Battery capacity calculations.

Supervisory power requirements for all equipment.

Alarm power requirements for all equipment.

Power supply rating justification showing power requirements for each of the system power supplies.

Justification showing power requirements of the system amplifiers.  Amplifiers shall be sized for a minimum of 1 watts per connected speaker in common areas and 0.5 watt per speaker in all other locations.

Voltage drop calculations for NAC wiring runs demonstrating worst-case condition.  Show capability of 25 or 70.7 vrms circuits for wire runs.

Provide complete battery calculations for both the alarm and supervisory power requirements.  Ampere hour requirements for each system component shall be submitted with the calculations.

[Provide detailed specific airflow balancing calculations for each of the air sampling smoke detectors.  Calculations shall be submitted with detailed drawings that indicate all sampling points, calculation nodes, and relevant information to allow complete review of the calculations against the detailed design drawings.]

FACP Wire Chart: Prepare a system wire chart.  Chart every wire showing the wire number, color, size, type of circuit, designation, origination point and termination point.  The chart shall be typewritten with minimum 12 point lettering on paper that is 8.5 inches by 11 inches.  The format of the wire chart shall be as shown on the contract drawings.  Provide one copy of the wire chart in a sealed plastic envelop inside the fire alarm control panel.

Terminal Cabinet Wire Chart:  Prepare a wire chart of the wires in each terminal cabinet.  Chart every wire showing the wire number, color, size, type of circuit, designation, origination point and termination point.  The chart shall be typewritten with minimum 12 point lettering.  The format of the wire chart shall be as shown on the contract drawings.  The chart must be protected with a clear laminate and mounted in each cabinet so that it does not interfere with the wiring or terminals.

Work Schedule: All work must be coordinated with facility operations.  Museum operations may require limited access to areas, arranging for museum security personnel to accompany contractors in non-public areas, and working during off-hours.  Prior to initial work, meet with museum staff to establish a work schedule. A work schedule must be submitted for approval prior to initial work.

Certificate of Compliance:  Within two weeks after passing the acceptance test submit a certificate of code and contract compliance to the COTR in accordance with NFPA 72, Paragraph 1-7.2.1.

QUALITY ASSURANCE

Manufacturer Qualifications

Testing Services or Laboratories:  Construct all fire alarm and fire detection equipment in accordance with the latest edition of the following publications from Underwriters Laboratories (UL) and Factory Mutual Engineering Corporation (FM):

UL Fire Protection Equipment Directory

UL Electrical Construction Materials Directory

UL 38 – Manually Actuated Signaling Boxes for Use With Fire Protection Signaling Systems

UL 228 – Door Holding Devices

UL 268 - Smoke Detectors for Fire Protective Signaling Systems

UL 268A - Smoke Detectors for Duct Application

UL 464 - Audible Signal Appliances

UL 497A – Secondary Protectors for Communications Circuits

UL 521 - Heat Detectors for Fire Protective Signaling Systems

UL 864 - Control Units for Fire Protective Signaling Systems

UL 1283 – Electromagnetic Interference Filters

UL 1449 -  Transient Voltage Surge Suppressors

UL 1480 - Speakers for Fire Protective Signaling Systems

UL 1971 - Signaling Devices for the Hearing Impaired

FM Approval Guide

Codes and Standards

International Building Code,  Latest Edition

Life Safety Code, Latest Edition

NFPA 70, National Electrical Code

NFPA 72, National Fire Alarm Code, 2002 Edition

Americans with Disabilities Act Accessibility Guidelines for Buildings and Facilities (ADAAG).

ASME/ANSI A 17.1, Safety Code for Elevators and Escalators

Qualifications of Installer:  Design shall be by a NICET Level III or IV Technician or a Registered Fire Protection Engineer.  Installer shall have an office, which has been in existence for at least 3 years, within a 75 mile radius of the U.S. Capitol. Installation shall be accomplished by an electrical contractor with a minimum of five years experience in the installation of fire alarm systems of similar size and capacity.  The services of a technician provided by the control equipment manufacturer shall be provided to supervise installation, adjustments, and tests of the system.

Distributor/ Service Organization/ Designer Qualifications:  Design Personnel certified by NICET as Fire Alarm Level III or IV. The manufacturer's equipment distributor shall show evidence of certification by the manufacturer in the technical support of the system installed under this contract.

The distributor shall show evidence of certification of at least one employee by the National Institute for Certification in Engineering Technologies (NICET) at Level III or IV in the Fire Alarm Systems subfield of Fire Protection Engineering Technology.  If such a certified individual is not employed, adequate documentation shall be provided to show comparable training and experience of an existing employee.  At a minimum, comparable training and experience shall consist of ten years of progressive experience in the installation and design of fire alarm systems of similar size and complexity to that specified herein.

In lieu of an employee with NICET Level III or IV certification, the distributor shall show evidence of at least one employee with a minimum of ten years of progressive experience in the design of fire alarm systems and, in addition, the distributor shall show evidence of technical support in the design, installation, and testing of the systems from a manufacturer-affiliated company, which shall show evidence of certification of at least one employee by the National Institute for Certification in Engineering Technologies (NICET) at level III or IV in the Fire Alarm Systems subfield of Fire Protection Engineering Technology.

The contractor shall furnish evidence that the fire alarm equipment supplier has an experienced and effective service organization, which carries a stock of repair parts for the system being furnished.  Should the Contractor fail to comply with the service requirements of this section, the Smithsonian will then have the option to make the necessary repairs and back-charge contractor without any loss of warranty as provided by the contract documents.

Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

DELIVERY STORAGE AND HANDLING

Deliver products to project site in original, unopened packages with intact and legible manufacturers’ labels identifying product and manufacturer, date of manufacture, and shelf life if applicable.

Store materials inside, under cover, above ground, and kept dry and protected from physical damage until ready for use. Remove from site and discard wet or damaged materials.

PROJECT CONDITIONS

Interruption of Existing Fire Alarm Service:  Do not interrupt fire alarm service to facilities occupied by The Smithsonian Institution or others unless permitted under the following conditions and then only after arranging to provide temporary guard service according to requirements indicated:

Notify COTR no fewer than two days in advance of proposed interruption of fire alarm service.

Do not proceed with interruption of fire alarm service without The Smithsonian Institution's written permission.

COORDINATION

Coordinate sprinkler head layout with reflected ceiling plan and all ceiling – mounted equipment, including diffusers, lights, security cameras, fire alarm devices, exit signs, and other devices.

Coordinate major equipments and piping layouts with other trades to avoid obstructions and excessive changes in direction for piping.

WARRANTY:

The contractor shall guarantee labor, materials, and equipment provided under this contract against defects for a period of one year after the date of final acceptance of this work by the Smithsonian and after the receipt of as-built drawings and schematics of all equipment.

SERVICE AGREEMENT

[List requirements, if part of the contract. Confirm with OSHEM and COTR].

EXTRA MATERIALS

Spare parts shall be directly interchangeable with the corresponding components of theinstalled system.  Spare parts shall be suitably packaged and identified by nameplate, stamping or tagging.

Furnish the following spare parts.  Quantity shall be two percent of the installed number of devices, but not less than the quantities listed:

Smoke Detectors of each type installed:  5

Heat detectors: 2

Manual pull stations:  2

Audio/visual devices: 5

Fuses for each fused circuit:  5

Electromagnetic door holder: 1

Spare rolls of paper for the system printer: 9 (plus sufficient paper for all fire alarm acceptance tests)

Lamps for each lamp type furnished:  5

Keys shall be provided for all fire alarm cabinets: 5

Wrenches or special tools required to gain access to all lockable equipment:  5

PRODUCTS

MANUFACTURERS

Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

FACP, cabinets, and peripheral devices:

EST

FireLite

Notofier

Siemens

Simplex Grinnell

Gamewell

FCI

Approved equal.

Wire and Cable: Comtran Corporation.

Helix/HiTemp Cables, Inc.; a Draka USA Company.

Rockbestos-Suprenant Cable Corporation; a Marmon Group Company.

West Penn Wire/CDT; a division of Cable Design Technologies.

Approved equal.

Conduit:

Allied

Approved equal

Boxes, supports, terminal blocks, and appurtenances:

As per Section Division 26

FIRE ALARM CONTROL PANEL (FACP):

The control panel shall be a U.L. listed Fire Alarm Control Panel with multiplex signaling service and voice evacuation.  All components shall be provided by one manufacturer.   As the central control unit for the entire system, the control panel shall provide power, supervision, control, and logic, utilizing solid state, modular components, internally mounted and arranged for easy access.  Each control unit shall be suitable for operation on a 120 volt, 60 hertz, normal building power supply.

Cabinet:  Install control panel components in cabinets large enough to accommodate all components and also to allow ample gutter space for interconnection of all panels as well as all field wiring.  The enclosure shall be identified by an engraved laminated phenolic resin nameplate.  Lettering on the nameplate shall say Fire Alarm Control Panel and shall not be less than 1-inch high.  If multiple panels are provided, additional identification shall be provided on each nameplate to distinguish the panels.  Provide prominent rigid plastic or metal identification plates for all lamps, circuits, meters, fuses and switches.  The cabinet shall be provided in a sturdy steel housing, complete with backbox, hinged steel door with cylinder lock, and surface mounting provisions.

Control/Display Modules:  Provide power and control modules in the FACP to perform all functions described in this specification.

Provide communication between the FACP and remote circuit interface panels, annunciators, and displays.

Non-volatile memory for system data base, logic, and operating system and event history.  The system shall require no manual input to initialize in the event of a complete power down condition.

Visual indication of alarm, supervisory or trouble initiation on the fire alarm control panel shall be by liquid crystal display or similar means with a minimum of 80 characters of which at least 32 are field changeable.

LED display for "ALARM", "AUDIBLE SILENCED", "SUPERVISORY", "TROUBLE", and "POWER ON".

Switches or buttons for "ALARM ACKNOWLEDGE", "AUDIBLE SILENCE", "SUPERVISORY ACKNOWLEDGE", "TROUBLE ACKNOWLEDGE", and "RESET"

[Programmable buttons or switches to perform custom functions such as drill, disable, bypass automatic control commands or other special functions as required by design.]

Programmable panel mounted relays to be software programmed to perform control functions required for system operation.

Notification appliance circuits as required to supervise and operate all connected notification appliances.  Operation of NACs shall be fully integrated with the FACP.  Switches shall be used to activate or deactivate speaker and strobe circuits.  Through the use of multi-colored LEDs, a clear indication shall be provided showing which circuits are active and to which strobe and audio channel.  The audio circuit shall activate a slow whoop tone for three cycles followed by a voice message which is repeated until the control panel is reset.   A live voice message shall override the automatic output through use of a microphone input at the control panel. The system shall be capable of operating all strobes and speakers at the same time.  The digitalized voice message shall consist of a non-volatile (EPROM) microprocessor based input to the amplifiers.  The microprocessor shall actively interrogate all circuitry, field wiring and digital coding necessary for the immediate and accurate rebroadcasting of the stored voice data into the appropriate amplifier input.  Loss of operating power, supervisory power or any other malfunction which could render the digitalized voice module inoperative shall automatically cause the slow whoop tone to take over all functions assigned to the failed unit.

Locate diodes and relays, if any, on screw terminals in the FACP.

Additional Requirements: The FACP shall have the following additional features:

System shall be UL 864 listed.

Field programmable.

Auxiliary Relays:  Provide sufficient SPDT auxiliary relay contacts for each detection zone to provide accessory functions as required.

Provide TROUBLE ACKNOWLEDGE, DRILL, and ALARM SILENCE switch.

Control panel shall have minimum 25% capacity for addition of future signaling line circuits and notification appliance circuits.  Each installed circuit shall have 20% spare capacity.

Analog Loop Driver to allow for continuous interrogation of each addressable device in the building.

Communication with auxiliary devices, including waterflow switches, valve supervisory switches, door controls, etc. through the use of appropriate interface modules as indicated on the riser diagram and interface schematics.

The FACP shall be listed for releasing service and shall be listed for connection to a Central Station Signaling System service.

The FACP shall have drift compensation technology and shall be UL listed as a calibrated smoke test instrument.

Device history shall be stored at the FACP.  At a minimum, the following information for each sensor shall be maintained:  device history, sensitivity levels, alarm verification status, drift compensation data.

The FACP shall provide a minimum 500 event history log.

The FACP shall indicate which communication zones have been silenced and shall provide selective silencing of alarm notification appliance by building communication zone.

Flow test shall be programmed as a software zone to permit de-activation of the audible alarms, and to activate and de-activate the flow test through the use of function keys at the panel.

All keys switches and panel buttons shall be programmed in accordance with the using agency’s specific requirements.

FIRE DETECTORS

Ionization and photoelectric light scattering type smoke detectors shall be provided as follows:

The detector shall be suitable for two wire 24VDC operation and two way communications on the intelligent analog signaling circuit.  Smoke detectors shall be U.L. listed for use with the FACP and environmental conditions

Detectors shall be self compensating for ambient temperature and humidity

Detector bases shall be installed on an industry standard, 4 inch (101 mm) square or octagonal electrical outlet box.  Bases shall be universal for ionization, heat, and photoelectric (light scattering type) detectors.

Detectors shall be twist lock type on to the base with self wiping contacts.

Screw clamp terminals shall be provided for all conductor terminations

The detector shall be addressed, tested and programmed prior to installation. The detector readout shall yield a discreet electrical value for status tracking and logging for determining maintenance and cleaning requirements.  An address to identify each detector, type, its location within the system, and its sensitivity setting.  The control panel shall provide a sensitivity readout from the detector without removal from the pluggable base.

Provide self-restoring type detectors which do not require any readjustment after actuation to restore them to normal operation.

All components shall be rust and corrosion resistant.  Vibration shall have no effect on the detector's operation.  Protect the detection chamber with a fine mesh metallic screen which prevents the entrance of insects or air born materials.  The screen shall not inhibit the movement of smoke particles into the chamber.

The detector shall display a steady LED when in the alarm state when the system is operating from normal or standby power.

Where selective localized control of electrical devices is required for interfaced equipment operation, furnish and install a base with software programmed addressable relay integral to the base.

Photoelectric - Beam Type:

Detectors shall be U.L. listed for use with the fire alarm control panel and environmental conditions.

Field programmable sensitivity settings of 20%, 35%, and 60% beam obscuration.

Latching alarm LED is built into the cover of the receiver or transmitter.

Compensation circuit for environmental variations.

Tied directly into an FACP control board.  A remote panel will not be allowed.

Duct Detectors:  Duct smoke detectors shall meet the requirements for photoelectric light scattering type detectors.  With the addition that duct detectors are U.L. listed for installation in air duct sampling housings for the detection of smoke in HVAC system ducts.

Heat Detectors:  Heat detectors in hoistways and elevator machine rooms shall be intelligent, low temperature (135ºF-140ºF), rate-compensating detectors.

The detectors furnished shall be U.L. listed for use in the FACP and environment conditions.

The detector shall be addressed, tested and programmed prior to installation.

The detector shall display a steady LED when in the alarm state when the system is operating from normal or standby power.

Detectors shall be equipped with screw terminals for each conductor.

Detectors shall be hermetically sealed and of the automatically resetting type which will operate when ambient air temperature reaches detector setting regardless of rate of temperature rise.

Detector operation shall not be subject to thermal lag.

AIR SAMPLING SMOKE DETECTOR:

General:

Air Sampling Scanner detector shall be laser based using a piping system and a fan to transport the particles of combustion to the detector.

There shall be 2 levels of alarm from each zone covered by the detector and one (1) trouble condition from each detector.

The air being sampled shall pass through a filter to reduce the amount of dust before entering the detection chamber.

Detector shall have the capability to connect to a network providing all data to the fire alarm control panel.  The air-sampling detector shall be connected to the building fire alarm system using interface modules, one for each level of alarm and one for common trouble.

All pipe airflow balancing calculations shall be performed using listed calculation software

Detector:

The Detector, Filter, Aspirator and Relay Outputs shall be housed in a mounting box and shall be arranged in such a way that air is drawn from the fire risk and a sample passed through the Dual Stage Filter and Detector by the Aspirator.

The Detector shall have an obscuration sensitivity range of 0.005 – 20% obs/m.

The Detector shall have four independent field programmable smoke alarm thresholds per pipe (sector) and a programmable scan time delay.

The laser based aspirating detection system shall have four (4) alarm thresholds per pipe (sector). The four alarm levels may be used as follows:

Alarm Level 1 (Alert)
Activate a visual and audible supervisory alarm.

Alarm Level 2 (Fire)
Activate General Building Alarm

Final detection system settings shall be approved by OSHEM. Initial Detection Alarm Settings shall be:

Alarm Level 1 (Alert)	0.08% Obs/m

Alarm Level 2 (Fire) 	2.0% Obs/m

Each pipe shall have its alarm thresholds set by a Sector Factor.  The Sector Factor range shall be between 0.5 and 2.0 (where 2.0 doubles the normal alarm threshold settings).

The system shall be powered from a regulated supply of nominally 24V DC.  The battery charger and battery shall comply with the relevant Codes, Standards or Regulations.  Twenty-four hours standby battery back up is required followed by 30 minutes in an alarm condition.

The Detector shall also incorporate facilities to transmit the following faults:

Detector

Air flow

Filter

System

Zone

Network

Power

Urgent and Minor faults.  Minor faults shall be considered as servicing or maintenance signals.  Urgent faults indicate the unit may not be able to detect smoke.

The detector shall have four in-line sample pipe inlets and must contain a flow sensor for each pipe inlet.  Both Minor and Urgent flow faults can be reported.

The aspirator shall be a purpose-designed rotary vane air pump. It shall be capable of allowing for multiple sampling pipe runs up to 200m in total, (4 pipe runs per detector) with a transport time of less than 120 seconds or as appropriate codes dictate.

The Assembly must contain relays for alarm and fault conditions. The relays shall be software programmable to the required functions.  The relays must be rated at 2 AMP at 30 VDC.  Remote relays shall be offered as an option and either configured to replicate those on the detector or programmed differently.

The Assembly shall be able to be surface mounted to a wall or recessed in the wall cavity (the unit may be inverted in either option).

The assembly shall have built-in event and smoke logging.  It shall store smoke levels, alarm conditions, operator actions and faults.  The date and time of each even shall be recorded.  Each detector (zone) shall be capable of storing up to 18,000 events and does not require the presence of a display in order to do so.

Displays:

A Display module shall be provided within each detector.

Each Display shall provide the following features at a minimum:

A bargraph display.

Four independent high intensity alarm indicators, Alert, Action, Fire 1 and Fire2, corresponding to the four alarm thresholds of the indicated sector.

Alarm threshold indicators for Alert, Action and Fire 1.

LED indication that the First Alarm Sector is established

Detector fault and airflow fault indicators.

Faults originating in the particular zone (Zone Fault) shall be distinguished from those produced by the overall smoke detection system and from those resulting from network wiring errors (Network Fault). LED indicators shall be provided for each fault category.

Minor and urgent fault LED indicators.

Sampling Tubes:

The sampling pipe shall be smooth bore with an internal diameter between 5/8 – 1 inch(15-25mm).  Normally, pipe with an outside diameter of 1” (25mm) and internal diameter of 7/8 inch (21mm) should be used.

The pipe material shall be CPVC and shall meet UL 1887, Fire Test of Plastic Sprinkler Pipe for Flame and Smoke Characteristics.

All joints in the sampling pipe must be air tight and made by using solvent cement, except at entry to the detector.

The pipe shall be identified with labels reading: “Aspirating Smoke Detector Pipe – Do not Paint or Disturb” (or similar wording) along its entire length at regular intervals not exceeding the manufacturers’ recommendation or that of local codes and standards.

All pipes should be supported at not less than 5 foot (1.5m) centers.

The far end of each trunk or branch pipe shall be fitted with an end cap and drilled with a hole appropriately sized to achieve the performance as specified and as calculated by the system design.

Sampling Holes

Sampling holes of 5/64 inch (2mm), or otherwise appropriately sized holes shall not be separated by more than the maximum distance allowable for conventional point detectors as specified in the local code or standard. Intervals may vary according to calculations.  Sampling hole layouts have been indicated on the plans.

Each sampling point shall be identified in accordance with Codes or Standards.

Consideration shall be given to the manufacturers recommendations and standards in relation to the number of Sampling Points and the distance of the Sampling Points from the ceiling or roof structure and forced ventilation systems.

MANUAL PULL STATIONS:

Provide double action intelligent manual stations where shown on the drawings, to be flush or surface mounted as required.  Manual stations shall be addressable.

Stations shall be equipped with terminal strip and pressure style screw terminals for the connection of field wiring.  Stations which require the replacement of any portion of the device after activation are not permitted.  Stations shall be finished in fire-engine red with molded raised lettering operating instructions of contrasting color.  The use of a key or wrench shall be required to reset the station.

A polycarbonate tamper cover shall be provided for pull stations located in public spaces.

NOTIFICATION APPLIANCES

Speakers and strobes shall be 24 or 70 VDC and shall be equipped with terminal strip and pressure style screw terminals for the connection of field wiring.  Devices shall be mounted to a 4 inch (101 mm) square outlet boxes.

Speakers:  Provide fire alarm speakers conforming to U.L. 464.

Speakers shall be provided with at least the following four tap settings: 2 watt, 1 watt, 1/2 watt, and 1/4 watt.

The audible signal shall have two alternate and distinct audible patterns; horn tone and recorded voice message; each field switchable for peak output levels of 100db  or 106db measured at 3048mm (10 feet).  When multiple tones are activated simultaneously, the tones shall be prioritized to avoid interference.

Strobe lights

Provide with red finish plate and with the word "FIRE" horizontally printed for ceiling mounting.

Xenon strobe with a minimum repetition rate of 1 HZ, not exceeding 3 HZ and a maximum duty cycle of 40% with a pulse duration of 0.2 seconds.

Visual alarm signals shall be furnished with minimum light intensity of 75 candela and meet the requirements of ADA and UL 1971.  In large rooms with ceilings over 10 feet, 110 candela models shall be provided.  Any device up to 110 cd shall have adjustable candela ratings.

Provide strobe light visual alarm signals which operate on 24 VDC.

Synchronization shall be provided as required in NFPA 72.

Audio-Visual Combination Assemblies shall be provided where strobes and speakers are identified at the same locations.

AMPLIFIERS, PREAMPLIFIERS, TONE GENERATORS:

General: Amplifiers, preamplifiers, tone generators, digitalized voice drives and all other hardware necessary for a complete, operational voice/alarm signaling service conforming to NFPA 72 shall be housed in a remote fire alarm control unit, terminal cabinet, or in the fire alarm control panel. Each amplifier shall have two channels; one to broadcast a message and the other for paging.

Construction: Amplifiers shall utilize solid state components and shall be provided with output protection devices sufficient to protect the amplifier against any transient up to ten (10) times the highest rated voltage in the system.

Inputs: Each system shall be equipped with separate inputs from the tone generator, digitalized voice driver and panel mounted microphone.  Microphone inputs shall be of the low impedance, balanced line type.  Both microphone and tone generator input shall be operational on any amplifier.

Tone Generator: The tone generator shall be of the modular, plug-in type with securely attached labels to identify the component as a tone generator and to identify the specific tone it produces.  The tone generator shall produce a slow whoop tone, which shall slowly ascend from low (500 hertz) to high (1200 hertz), and be constantly repeated until interrupted by either the digitalized voice message, the microphone input or the alarm silence mode as specified.  Each slow whoop cycle shall last approximately four (4) seconds.  The tone generator shall be single channel with an automatic backup generator per channel such that failure of the primary tone generator causes the backup generator to automatically take over the functions of the failed unit and also causes transfer of the common trouble relay.

Protection Circuits: Each amplifier shall be constantly supervised for any condition which could render the amplifier inoperable at its maximum output.  Failure of any component shall cause automatic transfer to a designated backup amplifier, illumination of a visual "amplifier trouble" indicator on the control panel, appropriate logging of the condition on the system printer and other actions for trouble conditions as specified.

[ELECTROMAGNETIC DOOR HOLDERS:

Where indicated on the drawings, provide magnetic fire door hold open devices.  The electromagnetic holding devices shall be designed to operate on 120 VAC, and require not more than 3 watts of power to develop 1.72 bar (25 psi) of holding force.

The initiation of nearby smoke detectors shall cause the release of the electromagnetic door holding device permitting the door to be closed by the door closer.  The door hold open devices shall release, allowing the doors to close upon receiving a signal from either: local smoke detectors, listed and labeled for the application; or the fire alarm system when the system receives a fire alarm signal from area detectors.

The initiating smoke detectors must be located within 1.5 m (5 ft) of the door hold open device as required by NFPA 72.

The device shall be U.L. listed based on U.L. 228 tests.

Each automatic door release must be provided with means of manual operation from a position at the door.

Door hold open devices must fail open, such that the door closes upon loss of power, or the holding device must have a secondary power source.

Where magnet extenders are installed, only the rigid type are permitted.

Doors fitted with release mechanisms must be provided with appropriate signage e.g. ‘Automatic Fire Door – Keep Clear’.]

[REMOTE PANELS:

Provide remote panels in the locations shown on the panels.

Remote panels shall meet the requirements listed under 2.02. Lettering on the nameplate shall say Remote Fire Alarm Control Unit.]

[GRAPHIC ANNUNCIATOR

Annunciator Panel:  Provide a graphic annunciator which indicates the building floor plan, including locations of stairs and elevators, control valve locations, and fire walls.  The boundaries for Indicating device circuits, HVAC zones, and sprinkler zones shall be clearly marked on the floor plan.  Annunciator shall include a north arrow and a "you are here" indicator.  The graphic annunciator shall be a minimum size of 3 feet by 3 feet (914 mm x 914 mm).

Indicating Lights:  Provide the graphic annunciator with individual LED indicating lights for each type of alarm and supervisory device.  Provide an amber LED for indicating a system trouble condition and a separate amber LED for indicating a supervisory condition.  Provide a green LED to indicate presence of power and a red LED to indicate an alarm condition.  The actuation of any alarm signal shall cause the illumination of a boundary LED, a floor LED, and a device LED.  System supervisory or trouble shall cause the illumination of a trouble LED.  In addition to all of these LED indicators, provide  emergency power indicating LED. Provide a push button LED test switch.  The test switch shall not require key operation.  Annunciator LEDs shall only be extinguished by operation of the system reset switch on the FACP.

Material:  Construct the graphic annunciator faceplate of smoked plexiglass.  The LEDs shall be backlit.  All control equipment and wiring shall be housed in a surface mounted backbox.  The exposed portions of the backbox shall be bronze plated with knockouts.

Programming:  Where programming for the operation of the proper LEDs is accomplished by a separate software program than the software for the fire alarm control panel, the software program shall not require reprogramming after loss of power.  The software shall be reprogrammable in the field.]

SYSTEM PRINTER

[The system printer shall be mounted within the FACP and visible through an opening in the enclosure door.  All printouts shall be automatically wound onto a take up spool.][The system printer shall be an external printer with associated printer stand.  Printer stand shall be capable of holding paper stock and shall provide a holding area for printouts.]

The printer shall continue to operate from building emergency power or fire alarm system standby batteries in the event of main power loss.

The printer shall record all system events including operator commands and shall be capable of providing a printed list of system conditions such as detector sensitivities, thresholds, analog voltages, device type, and custom message.  The printer shall automatically perform a self test every 24 hours.  A trouble condition shall be generated when printer paper has run out.  An internal buffer shall continue to store events when paper is out.

The printer shall have at least 80 characters per line and capable of printing at 120 characters per second.

REMOTE MONITORING SYSTEM:

All equipment device wiring shall be provided for remote monitoring.

FACP shall be compatible with remote monitoring station.

Communication between FACP and remote monitoring station shall be via [Ethernet][digital dialer].

POWER SUPPLIES

Primary power for the FACP shall be 120VAC service obtained from the emergency power panel board. Red colored breaker locks shall be provided for all fire alarm circuit breakers.

Secondary power for the FACP shall be provided by sealed gelled electrolyte batteries.  Batteries shall be housed in the control cabinet or a separate cabinet with adequate cell separation to prevent accidental discharge.

Battery Capacity: Battery supply shall be calculated to operate its load in a supervisory mode for twenty four hours with no primary power applied, and after that time, operate its alarm mode for five minutes. (In addition, an alarm reserve correction of 1.3 shall be included.)

Battery Charger:  Secondary power battery chargers shall be obtained from the emergency power panel board.  Provide battery charging circuitry for each standby battery bank in the system low voltage power supply or as a separate circuit.  The charger shall be automatic in design, adjusting the charge rate to the condition of the batteries.  Battery charge rate and terminal voltage shall be read using the fire alarm control panel LCD display in the service mode, indicating directly in volts and amps.  Charger shall be housed in the main fire alarm control panel or the battery cabinet.

LOAD CONTROL RELAYS:

Relays for the control of air handler contactors and elevator recall circuits shall be rated for use with circuits up to 240VAC at 7A inductive.  Relays shall be of the sealed pluggable type, and terminations shall be made to pressure type screw terminals.

INTERFACE MODULES:

Furnish intelligent analog signaling circuit interface modules for the monitoring of contact type initiation devices, the control of electrical devices, fire pump controllers, load control relays (controlling elevators and HVAC equipment), and each independent smoke detection, kitchen, and gaseous fire suppression systems.  The modules shall be capable of monitoring three separate functions:  alarm, trouble and supervisory conditions.

The module shall be addressed, tested and programmed prior to installation using a U.L. listed programmer/ tester.

The module shall display a steady LED for each circuit, in the normal power or standby power condition, when in the alarm state or during control circuit is activation.

[FIREFIGHTER TELEPHONE COMMUNICATION SYSTEM

Provide a firefighter telephone communication system with complete, common talk, closed circuits.  The system shall include, but not be limited to, a master control station mounted in the fire alarm control panel, a power supply and standby battery system, and remote telephone stations.

Provide a master control station which shall provide all power, supervision and control for all wiring, components, and circuits.  The act of lifting any remote telephone handset from its cradle shall cause both a visual and audible signal to annunciate at the master control station.  Removing the handset at the master control station and depressing a button at the remote telephone handset shall cause the automatic silencing of the audible signal.

Communication between the master control station handset and any/or all remote handsets shall require the depressing of a push-to-talk switch located on any/all remote handsets.  During the time that the master control handset is removed from its cradle it shall be possible to communicate between 5 remote handsets and the master control station.

Handsets shall be able to monitor any conversation in progress and join the conversation by pressing the push-to-talk button.  It shall not be possible to communicate between two or more remote handsets with the master control station handset in its cradle.  The master control station handset shall be red in color and equipped with a 5 foot (1524 mm) long strain-relieved coiled cord.  All wiring connections shall be made to terminal strips.

The master control station shall monitor all wire and connections for any opens, shorts or grounds which would render the system inoperable or unintelligible.  The master control station shall be equipped with a silencing switch and ring-back feature such that any audible trouble signal can be silenced and will be so indicated by the lighting of an amber LED.  Once any trouble condition has been corrected, the amber LED will be extinguished and the silence switch will sound again until the switch is restored to its original position.

The master control station shall be equipped with a separate, LED annunciated switch for each telephone circuit.  In addition, LEDs shall provide for the annunciation of operating and supervisory power.  The loss of operating or supervisory power shall cause an audible and visual indication at the master control station and shall also cause the fire alarm trouble signal to sound on the FACP.

All switches, LEDs and controls shall be fully labeled.

Provide surface or flush mounted remote telephone stations as indicated on the drawings.  Each station shall be equipped with a hinged door that is magnetically locked.  Each handset shall be permanently wired in place with a coiled cord.  Each handset shall be red high-impact cycolac and shall be equipped with a push-to talk switch which, when operated, will signal the master control station and a switch-equipped, storage cradle.]

EXECUTION

PRIMARY POWER:

Make the service connection for the FACP at the emergency distribution panel where shown.  Provide a separate NEMA 1 "General Purpose Enclosure" for the circuit breaker.  The circuit breaker enclosure shall be painted red, marked "FACP", and provided with a lockable handle or cover.

SYSTEM FIELD WIRING AND CONDUIT

Wiring Within Cabinets and Junction Boxes:  Provide wiring installed in a neat and workmanlike manner and installed parallel with or at right angles to the sides and back of any box or cabinet.

Conductor Type and Size: Wire size shall be sufficient to prevent voltage drop problems.  Wire type and sizing of conductors shall be in accordance with the manufacturers wiring specifications for the system, except for minimum wire size shall be as follows:

Signaling Line Circuits:			16AWG, Type FPLR, solid copper, shielded

Notification Appliance Circuits:14AWG, Type FPLR, solid copper, twisted pair, shielded

120VAC Circuits:				12AWG, Type THHN, solid copper

Interfaced Circuits:			      16AWG, Type FPLR, solid copper, shielded

Speaker Circuits:				16 AWG, Type FPLR, solid copper, twisted pair,unshielded

Firefighter Telephone Circuits:	18 AWG, solid copper, twisted pair

Battery Cable:					14 AWG, stranded

Connectors: All conductors shall be terminated at a screwed connector on a securely mounted approved pressure type terminal block.  The use of wire nuts or similar devices shall be prohibited.

Terminal Cabinets:  Provide a terminal cabinet at the base of any circuit riser, on each floor at each riser, and where indicated on the drawings.  Cabinet size shall be appropriate for the size of the wiring to be connected.

Conductor Numbering: All conductors installed in the system shall be numbered at every junction point.  Use a numbered shrink-wrap label designed specifically for this purpose.  Wire numbers shall be the same as those designated on the as-built drawings.  Mark each terminal in accordance with the wiring chart and diagrams of the system.

Conductor Color Coding: Color coded conductors shall be consistent for each type of circuit.  When renovating or adding to an existing system, color coding shall match the existing system.

Signaling Line and Notification Appliance Circuits

Signaling Line, notification appliance, and power circuits shall each be in separate conduit.

Strobes are to be connected to circuits separate from speakers. This includes strobes and speakers that are mounted as a unit.

Provisions for tying-in signaling line and notification appliance circuits directly to the FACP mother board (board containing CPU) shall not be used.  Initiation and indicating circuits shall be tied to a separate electronic board before connection to the mother board.

Circuit Loading:

Spare capacity shall be in accordance with 1.07.

Circuits operating at 24VDC shall not operate at less than 21.6volts.  Circuits operating at any other voltage shall not have a voltage drop exceeding 10% of nominal voltage.

Spare Circuits: Provide one spare signaling line and notification appliance circuit for each terminal box placed at each floor on each riser.  Spare capacity shall also be provided in the FACP for these circuits.  FACP control boards shall be provided to permit 2 spare initiation circuits and 2 spare indicating circuits.  Spare circuits are not to include those provided on the mother board.

Wiring to a Central Station: Provide a dedicated telephone line from the FACP modem to the central monitoring panel in the South Quadrangle building.

Conduit:

All conductors shall be in grounded metal conduit.  Conduit shall be Rigid metal or EMT.  Flexible metal conduit not exceeding six foot lengths shall be permitted from junction box to initiating device.  On flexible metal conduit, use only insulated throat connectors.

Run conduit or tubing concealed unless specifically shown otherwise on the drawings.

Minimum conduit size shall be 3/4-inch.

Circuits to Interfaced Equipment:

Circuits to smoke management systems, fan shutdown systems, door locking systems, A/V shutdown, fire door release, and firefighter telephones in elevator cabs shall terminate in terminal cabinets within 914mm (3 feet) of the controllers for those systems.  The completion of those circuits from the terminal cabinets to the appropriate system shall be provided under the appropriate division specification.

Load Control Relays:

All relays shall be supervised as required by NFPA 101 and mounted within three feet of the device controlled.

FIRESTOPPING:

Seal all holes caused by penetrating conduit, piping, or other penetrations which pass through floors, walls or ceilings.  Firestop penetrations through floor slabs, fire-rated walls, shafts, or any fire-rated assembly in accordance with Section 078413, Penetration Firestopping.

MARKING:

All metal surfaces shall be painted.  Metal conduit in finished areas shall be painted the color to match adjacent surfaces.  Junction boxes in unfinished areas shall be painted a full gloss enamel red.  Painting shall be in accordance with Section 099000.

Red bands shall be applied every 10 feet (3.05m) when not using red-colored conduit.

Prior to acceptance testing each fire alarm initiating device must be labeled with the device address.

DEVICE INSTALLATION:

FACP:  Locate the FACP where indicated on the drawings.  Surface mount the enclosure with the top of the cabinet 6 feet (1829 mm)  above the finished floor or center the cabinet at 5 ½ feet (1676 mm ), whichever is lower.

Manual Pull Stations: Mount the manual pull stations so that their operating handles are 4 feet (1219 mm) above the finished floor.

Strobes:  Wall mount strobes shall be a minimum of 80 inches (2032 mm) above the finished floor or 6 inches (152 mm) below the ceiling whichever is lower.

Speakers:  Speakers should typically be set on the 1/2 watt tap.  Speakers in areas with ceilings above 3048 mm (10 feet) shall be set on the 3/4 watt tap.   Install speakers in elevator cabs.

Smoke Detectors:

In raised floor spaces, the smoke detectors shall be installed to protect 225 sq. ft (145161 sq. mm) per detector.

In hallways, open areas, and rooms where more than two smoke detectors are located, ionization type detectors and photoelectric type detectors shall be installed.  These detectors should be arranged so that every other detector in the room is a different type than the adjacent detector.  In single detector rooms install an ionization detector.

Photoelectric type detectors shall be installed in elevator machine rooms and elevator hoistways.

Install smoke detectors a minimum of 3 feet (914 mm) away from supply air vents.

New smoke detectors shall be installed with dust covers.  The dust covers shall be removed just prior to acceptance testing.

The indicating LED on the smoke detector shall be visible from the floor.  Where ceiling conditions prevent easy viewing of the LED from the floor, a remote indicating lamp must be installed.

Heat Detectors for Elevator Rooms and Shafts:  Heat detectors, provided to meet ANSI A17.1 requirements for elevator power disconnect, shall be located within 2 feet of each sprinkler head.

Graphic Annunciator:  Surface mount the panel, with the top of the panel 6 feet (1800 mm) above the finished floor or center the panel at 5 ½ feet (1600 mm), whichever is lower.

[Firefighter Telephones:

Locate wall mounted in each stair at each floor landing, in each elevator lobby and in each elevator cab 4 feet above the finished floor.]

Audio-Visual Equipment Shunt Switches:

Smoke detectors are to be installed in enclosed AV booths/rooms.  Activation of the smoke detector is to shut-down power to the A/V equipment.  Self-contained units (not tied to the FACP) with a local alarm are permitted.

Activation of the general fire alarm shall shut-down all AV equipment.  This is so that audio portions of A/V equipment do not compete with the fire alarm system.  This is easily done if the A/V control circuits are central to one panel or area.  A circuit is required from the FACP to relays to the central A/V control circuits to shunt power.

Door Hold-Open/Release Devices:

Relays shall be mounted within three feet of the device controlled.

Smoke detectors with integral relays shall control the door hold-open devices.

Load Control Relays:  Relays for elevator shunt and HVAC control shall be mounted in a NEMA style enclosure, painted red, and appropriately labeled, such as, BRKR SHUNT RELAY.

[Elevator Cab Fire Alarms: Elevator cab speakers, strobes, and firefighters telephones shall be turned over to the elevator contractor whose work is described in Division 16.  Coordinate provision for traveling cables and other installation accessories for connection of these devices.]

TESTS

Megger Tests:  After all wiring has been installed, and prior to making any connections to panels or devices, all wiring shall be megger tested for insulation resistance, grounds, and/or shorts.  Conductors with 300 volt rated insulation shall be tested at a minimum of 250 VDC.  Conductors with 600 volt rated insulation shall be tested at a minimum of 500 VDC.  The tests shall be witnessed by OSHEM and the Contracting Officer and test results recorded for use at the final acceptance test.

Loop Resistance Tests:  Measure and record the resistance of each circuit with each pair of conductors in the circuit short-circuited at the farthest point from the circuit origin.  The tests shall be witnessed by the Contracting Officer and OSHEM and test results recorded for use at the final acceptance test.

Preliminary Testing:  Conduct preliminary tests to ensure that all devices and circuits are functioning properly.   After preliminary testing is complete, provide a letter certifying that the installation is complete and fully operable.  The letter shall state that each initiating and indicating device was tested in place and functioned properly.  The letter shall also state that all panel functions were tested and operated properly.  The Contractor and an authorized representative from each supplier of equipment shall be in attendance at the preliminary testing to make necessary adjustments.

Final Acceptance Test:  Notify the Contracting Officer in writing when the system is ready for final acceptance testing.  Submit request for test at least 14 calendar days prior to the test date.  A final acceptance test will not be scheduled until meggar test results, the loop resistance test results, and the submittals required in Part 1 are provided to the Contracting Officer.  Test the system in accordance with the procedures outlined in NFPA 72.  The required tests are as follows:

Verify the absence of unwanted voltages between circuit conductors and ground.

Verify that the control unit is in the normal condition as detailed in the manufacturer's operating and maintenance manual.

Complete operational tests under emergency generator power

Complete operational tests under battery power and as described above under battery power. Test the battery charger.

Test each initiating and indicating device and circuit for proper operation and response.  Disconnect the confirmation feature for smoke detectors during tests to minimize the amount of smoke or test gas needed to activate the detector.

Test the system for all specified functions in accordance with the contract drawings and specifications and the manufacturer's operating and maintenance manual.

Visually inspect all wiring.

Verify that all software control and data files have been entered or programmed into the FACP.

Verify that Shop Drawings reflecting as-built conditions are accurate.

Measure the current in circuits to assure that there is the calculated spare capacity for the circuits.

Measure voltage readings for circuits to assure that voltage drop is not excessive.

Measure the voltage drop at the most remote appliance on each notification appliance circuit.

Test Equipment: The contractor shall supply personnel, communication devices, and all equipment necessary for performance of the final test.

TRAINING

Instructor:  Include in the project the services of an instructor, who shall have received specific training from the manufacturer for the training of other persons regarding the inspection, testing and maintenance of the system provided.  The instructor shall train the Smithsonian employees designated by the Contracting Officer, in the care, adjustment, maintenance, and operation of the fire alarm system.

Training sessions shall cover all aspects of system performance, including system architecture, signaling line circuit configurations, sensor and other initiating device types, locations, and addresses, fire alarm control panel function key operation, and other functions as designated by the COTR.

Required Instruction Time:  Provide 16 hours of instruction after final acceptance of the system.  The instruction shall be given during regular working hours on such dates and times as are selected by the Contracting Officer.  The instruction may be divided into two or more periods at the discretion of the Contracting Officer. One training session shall be videotaped by the contractor. Videotapes shall be delivered to the COTR.

Provide a typeset printed or typewritten instruction card mounted behind a Lexan plastic or glass cover in a stainless steel or aluminum frame.  Install the frame in a conspicuous location observable from the FACP.  The card shall show those steps to be taken by an operator when a signal is received as well as the functional operation of the system under all conditions, normal, alarm, supervisory and trouble.  The instructions shall be approved by the COTR.

Comprehensive system troubleshooting training shall be provided for a single individual designated by the COTR.  This session shall be separate and distinct from the above described sessions.

All training sessions shall be conducted following final system certification and acceptance.  Three additional training sessions shall be provided for all security personnel on all shifts six months after final system certification.

All training sessions shall be conducted by an authorized fire alarm system distributor representative, who has received specific training from the manufacturer for the training of other persons regarding the inspection, testing, and maintenance of the system provided.

KEYS

Keys and locks for all equipment shall be identical where possible.  Provide not less than six keys of each type required.  Identify keys by an appropriate number stamped on each key or on a metal tag attached thereto.  Provide a key numbering chart in each operation and maintenance manual furnished.

END OF SECTION 283111