# FIRE DETECTION AND ALARM SYSTEMS

Inspections, tests, and maintenance on fire detection and alarm systems shall be performed in accordance with the manufacturer's instructions and NFPA 72 (latest edition).  The following list highlights minimum requirements for the essential care of fire alarm systems.  This list, however, is not meant to replace manufacturer's instructions and updated code requirements.

ITEM					ACTIVITY	   FREQUENCY           NFPA 72, 		 										           TABLE 10.3.1 Item #

Alarm Notification Appliances	Inspection		Semiannually							13

Batteries  (Fire Alarm Systems)

Lead-acid type			Inspection			 Monthly						3

Nickel-cadmium type		Inspection				Semiannually				3

Primary type (Dry cell)		Inspection	  			Monthly					3

Sealed-lead acid type		Inspection  				Semiannually				3

Control Equipment (FA systems

monitored for alarm, supervisory,

trouble signals)

Fuses				Inspection			Annually					1

Interfaced equipment		Inspection			Annually					1

Lamps and LEDs			Inspection			Annually					1

Primary (main) power supply	Inspection			Annually					1

Control panel trouble signals		Inspection			Semiannually				5

Emergency voice/Alarm		Inspection			Semiannually				7

communications equipment

Fiber optic cable connections		Inspection			Annually					6

Initiation devices

Air sampling						Inspection					Semiannually				9

Duct detectors						Inspection					Semiannually				9

Electromechanical releasing dev.	Inspection					Semiannually				9

Extinguishing systems switches		Inspection					Semiannually				9

Fire alarm boxes						Inspection					Semiannually				9

Heat detectors						Inspection					Semiannually				9

Radiant energy fire detectors		Inspection					Quarterly					9

Smoke detectors						Inspection					Semiannually				9

Supervisory signal devices			Inspection					Quarterly					9

Waterflow devices					Inspection					Quarterly					9

ITEM					ACTIVITY		FREQUENCY	   	NFPA 72 												        TABLE 10.3.1, Item #

Interface equipment					Inspection				Semiannually				12

Remote annunciators					Inspection				Semiannually			8

Special procedures					Inspection				Semiannually				16

Transient suppressors					Inspection				Semiannually				4

Supervising Station FA Systems-

Transmitters

DACT  								Inspection				Semiannually				15

DART  								Inspection				Semiannually  				15

McCulloh							Inspection				Semiannually				15

RAT - signal receipt					Inspection				Semiannually 				15

Supervising Station FA Systems-

Receivers

DACR								Inspection				Monthly					17

DARR								Inspection				Semiannually				17

McCulloh							Inspection				Semiannually				17

Two-way RF						Inspection				Semiannually				17

PASSR								Inspection				Semiannually				17

RARS								Inspection				Semiannually				17

Private Microwave					Inspection				Semiannually				17

ITEM					ACTIVITY		FREQUENCY		NFPA 72 												          TABLE 10.4.4 Item #

Alarm notification appliances																			    19

Audible devices			Test			Annually

Audible textual appliances		Test			Annually

Visible devices			Test			Annually

Batteries  (Fire Alarm Systems)

Lead-acid type														6a

Charger test	(replace as needed)	Test			Annually

Discharge test (30 min.)		Test			Semiannually

Load voltage test			Test			Semiannually

Specific gravity			Test			Semiannually

Nickel-cadmium type													6b

Charger test	(replace as needed)	Test			Annually

Discharge test (30 min.)		Test			Annually

Load voltage test			Test			Semiannually

Primary type (dry cell)												6c

Age test				Test			Monthly

Sealed lead-acid type													6d

Charger test	(replace w/in 5 yrs.)	Test			Annually

Replace battery			Replace		Every 5 years

Discharge test (30 min)		Test			Annually

Load voltage test			Test			Semiannually

Control Equipment (connected to 											1

supervising station)

Functions				Test			Annually

Fuses				Test			Annually

Interfaced equipment		Test			Annually

Lamps and LEDs			Test			Annually

Primary (main) power supply	Test			Annually

Transponders			Test			Annually

Control Equipment (not connected  											2

to supervising station)

Functions				Test			Quarterly

Fuses				Test			Quarterly

Interfaced equipment		Test			Quarterly

Lamps and LEDs			Test			Quarterly

Primary (main) power supply	Test			Quarterly

Transponders			Test			Quarterly

Engine Driven Generator		Test			Monthly				3

Control unit trouble signals		Test			Annually					9

ITEM					ACTIVITY		FREQUENCY	           NFPA 72  										                                 TABLE 10.4.4, Item #

Emergency voice/Alarm		Test			Semi-annually1	                 12

communications equipment

Fiber optic cable power		Test			 Annually					8

Initiation devices														15

Duct detectors						Test					Annually

Electromech. releasing devices		Test					Annually

Extinguishing systems switches		Test					Annually

Fire-gas and other detectors			Test					Annually

heat detectors						Test					Annually

fire alarm boxes						Test					Annually

radiant energy fire detectors			Test						Semiannually

smoke detectors - functional		Test						Annually

smoke detectors - sensitivity		Test						Biannually

(see 10.4.3.2)

single & multi-station smoke		Test						Annually

alarms (also see 10.4.4)

single and multi-station heat alarms  Test						Annually

supervisory signal devices			Test						Quarterly

waterflow devices					Test						Quarterly2

valve tamper switches				Test						Semiannually

Interface equipment					Test					Annually						18

Off-premises transmission equip.		Test					Quarterly									22

Remote annunciators					Test					Annually						14

Special hazard equipment				Test					Annually							19

Special procedures					Test					Annually						24

Supervising station fire alarm																				23

systems – Transmitters

DACT								Test					Quarterly3

DART								Test					Quarterly3

McCulloh							Test					Quarterly3

RAT								Test					Quarterly3

Supervising station fire alarm																				25

systems – Receivers

DACR								Test					Monthly

DARR								Test					Monthly

McCulloh							Test					Monthly

Two-way RF multiplex			Test					Monthly

ITEM					ACTIVITY		FREQUENCY	            NFPA 72  											          TABLE 10.4.4 Item #

Supervising station fire alarm																			25

systems – Receivers (continued)

RASSR								Test					Monthly

RARSR							Test					Monthly

Private microwave					Test					Monthly

1		Due to frequency of construction and system modifications which occur in the museums, testing was increased from annually to semi-annually for voice/alarm communications equipment.

2		Testing frequency adjusted to match NFPA 25 requirements for waterflow devices.

3	    Testing frequency increased to quarterly due to history of trouble contacts being disconnected.

- Data is based on 2007 edition