STANDPIPE AND HOSE SYSTEMS

Inspections, tests, and maintenance on standpipe and hose systems shall be performed in accordance with the manufacturer's instructions and NFPA 25 (latest edition).  The following list highlights minimum requirements for the essential care of standpipe and hose systems.  This list, however, is not meant to replace manufacturer's instructions and updated code requirements.

ITEM				ACTIVITY	FREQUENCY                NFPA 25

Control valves			Inspection		Weekly/monthly		Table 12.1

Pressure regulating devices	Inspection		Quarterly			Table 12.1

Piping				Inspection		Quarterly			6.2.1

Hose connections		Inspection		Quarterly			Table 12.1

Cabinet			Inspection		Annually				NFPA 1962

Hose*				Inspection		Annually				NFPA 1962

Hose storage device*		Inspection		Annually				NFPA 1962

Alarm device			Test			Quarterly			Table 12.1

Hose nozzle*			Test			Annually				NFPA 1962

Hose storage device*		Test			Annually				NFPA 1962

Hose*				Test			5 years/3 years1		NFPA 1962

Pressure control valve		Test			5 years					Table 12.1

Pressure reducing valve	Test			5 years					Table 12.1

Hydrostatic test		Test			5 years					6.3.2

Flow test			Test			5 years					6.3.1

Main drain test		Test			Annually				Table 12.1

Hose connections		Maintenance		Annually				Table 6.2.2

Valves (all types)		Maintenance		Annually/as needed		Table 12.1

*	Hose and nozzle requirements determined by the local AHJ.  Hoses not required for 	Smithsonian buildings within the District of Columbia.

1  Hose test required within 5 years of date of manufacture and every 3 years thereafter.

- Based on 2002 edition