WATER STORAGE TANKS USED FOR FIRE PROTECTION

Inspections, tests, and maintenance of water storage tanks used for fire protection shall be performed in accordance with the manufacturer's instructions and NFPA 25 (latest edition).  The following list highlights minimum requirements for the essential care of water storage tanks.  This list, however, is not meant to replace manufacturer's instructions and updated code requirements.

ITEM				ACTIVITY		FREQUENCY		      NFPA 25

Condition of water in tank	Inspection		Monthly/quarterly		9.2.1

Water temperature		Inspection		Daily/weekly				9.2.4

Heating system		Inspection		Daily/weekly				9.2.6.6

Control valves			Inspection		Weekly/monthly			Table 12.1

Water level			Inspection		Monthly/quarterly			9.2.1

Air pressure			Inspection		Monthly/quarterly			9.2.2

Tank - exterior		Inspection		Quarterly				9.2.5.1

Support structure		Inspection		Quarterly				9.2.5.1

Catwalks and ladders		Inspection		Quarterly				9.2.5.1

Surrounding area		Inspection		Quarterly				9.2.5.2

Hoops and grillage		Inspection		Annually				9.2.5.4

Painted/coated surfaces	Inspection		Annually				9.2.5.5

Expansion joints		Inspection		Annually				9.2.5.3

Interior			Inspection		5 years/3 years	1			9.2.6

Check valves			Inspection		5 years					Table 12.1

Temperature alarms		Test			Monthly				9.2.4.2, 9.2.4.3

High temp. limit switches	Test			Monthly				9.3.4

Water level alarms		Test			Semiannually				9.3.5

Level indicators		Test			5 years					9.3.1

Pressure gauges		Test			5 years					9.3.6

Water level			Maintenance		Continuous				9.4.1

Drain silt			Maintenance		Semiannually				9.4.5

ITEM				ACTIVITY	    FREQUENCY		       NFPA 25

Control valves			Maintenance		Annually			  Table 12.1

Embankment supported

rubberized fabric		Maintenance		2 years2				9.4.6

Check valves			Maintenance	Per manuf. instructions			12.4.2.2

1 Tanks with interior corrosion protection require inspection every 5 years.  All other tanks   require interiors to be

inspected every 3 years.

2 Maintain ESCF tanks per manufacturer’s instructions.  Clean and paint exposed surfaces every 2 years.

- Data is based on 2002 edition.