FIRE DOORS AND EMERGENCY EXITS

Inspections, tests, and maintenance shall be performed on fire doors and emergency exits in accordance with the manufacturer's instructions, NFPA 101 (latest edition), and NFPA 80 (latest edition).  The following list highlights minimum requirements for the essential care of fire doors and emergency exits.  This list, however, is not meant to replace manufacturer's instructions and updated code requirements.

Emergency exits must be maintained to avoid the numerous deaths caused in fires where exits were either blocked or the hardware was inoperable.  In addition, fire doors have no value unless properly maintained and closed or able to close automatically at the time of a fire.

## ITEM						ACTIVITY	FREQUENCY	NFPA REF.

Fire Doors:

Door hardware is operating properly		Inspection	Annually		80:5.2.4 & 5.2.5

Door does not have punctures or		Inspection	Annually		80:5.2.4 & 5.2.5

broken seams.

Self-closer is intact and allows door		Inspection	Annually		80:5.2.4 & 5.2.5

to latch closed.

On sliding doors, chains and cables		Inspection	Annually		80:5.2.4 & 5.2.5

operate smoothly over all pulleys

and guides.

Doors have not been modified		Inspection	Annually		80:5.2.4 & 5.2.5

e.g., by the installation of louvers.

Coordinators are securely attached	Inspection	Annually		80:5.2.4 & 5.2.5

and adjusted properly.

Door openings are kept clear of		Inspection	Semi-annually1		80:5.2.13

obstructions.

Clearances around the door do 		Inspection	Annually		80:5.2.4 & 5.2.5

not exceed NFPA 80 requirements

Tinclad and Kalamein doors 		Inspection	Annually	80:5.2.10

Doors are kept closed or arranged		Inspection	Semi-annually1	80:5.2.14

for automatic closing

Confirm proper operation of doors		Test		Annually	80:5.2.6

with hold open devices and self-closers

(Latches, guides and rollers

must be checked.)

Test all horizontal, sliding, and rolling 	Test		Annually		80:5.2.14

fire doors

Lubricate guides and bearings.		Maintenance	Annually	80:5.2.12

Emergency exit doors (perimeter exits and doors with delayed egress hardware):

Not obstructed				Inspect			Weekly	101:4.5.3.2

Hardware operating	 properly			Test			Weekly	101:7.2.1.4

Measure door opening force.  (Force 	   Test			Quarterly	101:7.2.1.4

gauge used to ensure door can be

opened within NFPA 101 limits.)

Stairwell doors (interior):

Not obstructed				Inspect			Quarterly	101:4.5.3.2

Hardware operating properly			Test			Quarterly	101:7.2.1.4

Measure door opening force.  (Force 	   Test			Annually	101:7.2.1.4

gauge used to ensure door can be

opened within NFPA 101 limits.)

1	To be completed during each annual Safety Coordinator and safety committee inspection

- Data is based on NFPA 101 (2007), 80 (2007) edition.