DIVISION 2

SECTION 028200 - ASBESTOS ABATEMENT

PART 1 - GENERAL

1.1   Introduction

1.2   Description of the Abatement Work

1.3   Definitions

1.4   Regulations and References

1.5   Submittals

1.6   Daily Reports

1.7   Product Handling

PART 2 - PRODUCTS

2.1   Materials

2.2   Equipment

PART 3 - EXECUTION

3.1   Controlled Access to Site

3.2   Worker and Visitor Protection

3.3   Abatement Work Area Entry and Exit Procedures

3.4   Respiratory Protection

3.5   Air Monitoring; Stop Action and Clearance Levels

3.6   Initial Isolation of Abatement Work Area

3.7   Preparation of Abatement Work Area and Temporary Enclosures

3.8   Construction of Worker/Equipment Decontamination and Waste

Load-Out Enclosures

3.9   Air Circulation Inside Containment Barrier

3.10  Placement of Air Filtration System Units

3.11  Pressure Differential Isolation

3.12  Pre-Abatement Inspection, Testing, and Approval

3.13  Maintenance of Containment Barrier and Enclosures

3.14  Removal of Asbestos-Containing Materials (ACM) - General

3.15  Requirements for Specific ACM and Methods - Fireproofing/

Soundproofing on Scratch Coat or Wire Lath

3.16  Requirements for Specific ACM and Methods - Vinyl Asbestos Tile

(VAT) and Mastic

3.17  Requirements for Specific ACM and Methods - Roofing

3.18	Requirements for Specific ACM and Methods - Exterior and Interior

Window Caulk……………………………………………………………….32

3.19  Requirements for Specific ACM and Methods - Gypsum Wallboard

Joint Compound

3.20  Requirements for Specific ACM and Methods - Duct Insulation Mastic

3.21  Requirements for Specific ACM and Methods - Contaminated Soils

3.22  Requirements for Specific ACM and Methods - Contaminated Carpeting

3.23  Requirements for Specific ACM and Methods - Removal of

Asbestos-Containing Transite Panels.

3.24  Requirements for Specific ACM and Methods - Glove-Bag Removal

Method

3.25  Requirements for Specific ACM Methods:  Negative Pressure Glove

Box Systems

3.26  Requirement for Specific ACM Methods:  Water Spray Process System

3.27  Requirement for Specific ACM Methods:  Mini Enclosure

3.28  Requirements for Specific ACM and Methods - Dry-Removal of

Electrical Equipment

3.29  Post Removal:  Cleaning and Clearance

3.30  Post Clearance:  Application of Lockdown Encapsulant To Base Material	41

3.31  Containment Barrier Removal

3.32  Waste Disposal

3.33  Job Close-Out	44

DIVISION 2

SECTION 028200- ASBESTOS ABATEMENT

PART 1 - GENERAL

1.1	Introduction

1.1.1	Perform all planning, administration, execution, and cleaning necessary to safely remove asbestos-containing or contaminated materials.

1.1.2	Approval of or acceptance by the Contracting Officer’s Technical Representative (COTR) of various construction activities or methods proposed by Contractor does not constitute an assumption of liability either by the COTR or Smithsonian Institution (SI) for adequacy or adverse consequences of said activities or methods.

1.2	Description of the Abatement Work

1.2.1	The asbestos abatement shall also include, but not be limited to the following:

(a)	Notification to regulatory agencies

(b)	Regulatory permits, licenses and approvals

(c)	Worker health and safety program

(d)	Air monitoring

(e)	Construction of temporary containment

barrier/decontamination enclosures

(f)	Preparation for abatement operations

(g)	Removal of existing asbestos-containing

material

(h)	Transport and disposal of asbestos-containing

material

(i)	Decontamination and cleaning

(j)	Application of lockdown encapsulants

(k)	Removal of temporary containment

barrier/decontamination enclosures

(l)	Final job close-out

1.2.2	Summary Listing of Work Locations and Approximate Quantity: The Contractor shall review all contract documents and make a site visit to make his/her own determination about quantity values prior to applying for the required federal, state, or local permits from agencies having authority or jurisdiction.

1.2.3	Drawings and Other Information:  Drawings of the project area(s) and the reference location(s) within the building may be provided upon request to assist in the Contractor's planning of the abatement work effort for protection of occupants and contents.

1.2.4	Other Work Not Included:  Concurrently with this contract, the SI reserves the right to collect and analyze samples or retain an independent testing laboratory to provide supplemental sampling services.  These services will in no way relieve the Contractor from compliance liability or from providing the testing required by these specifications or any other requirements of other agencies with jurisdiction authority.

NOTE:	  The SI has contracted independent air monitoring and testing services. The Contractor shall use a different firm for air monitoring and testing on this project.

1.3	Definitions

1.3.1	Abatement:  Procedures to control or eliminate fiber release from asbestos-containing building materials, to include encapsulation, enclosure and removal.

1.3.2	Abatement Work Area (regulated area):  An area established by the employer to demarcate areas where Class I, II, III and IV asbestos work is conducted, and any adjoining area where debris and waste from such asbestos work accumulate; and a work area within which airborne concentrations of asbestos, exceed or there is a reasonable possibility they may exceed the permissible exposure limit.

1.3.3	Airlock:  A system of enclosures within the containment area consisting of two (2) doorways, curtained with polyethylene sheeting, at least 1 meter apart.

1.3.4	Air Filtration Units:  A local exhaust unit, utilizing high-efficiency particulate air (HEPA) filtration and capable of maintaining a minimum negative pressure differential of 0.05 mm of water within the containment barrier with respect to that of the environment surrounding the containment barrier.  The unit also cleans recirculated air or generates a constant air flow from adjacent areas into the abatement work area through the decontamination enclosure.

1.3.5	Air Monitoring:  The process of measuring the fiber content of a specific volume of air during a stated period of time.

1.3.6	Air Pressure Monitoring:  The process of measuring the air pressure differential between the containment barrier and the surrounding area using a micromanometer unit.

1.3.7	Amended Water:  Water to which a surfactant (wetting agent) has been added to increase the ability of the liquid to penetrate asbestos containing materials (ACM).

1.3.8	ANSI:  American National Standards Institute.

1.3.9	ASTM:  American Society for Testing and Materials.

1.3.10	Asbestos:  Asbestiform varieties of chrysotile, amosite, crocidolite, tremolite, anthophyllite, and actinolite.

1.3.11	Asbestos-Containing Material (ACM):  Any material containing more than 1% asbestos by volume of any type or mixture of types.

1.3.12	Authorized Person:  Any person authorized by the SI and required by work duties to be present in a regulated area.

1.3.13	Caulking:  High-grade rubber base caulk for masonry and/or for other materials to be used or existing, as appropriate.

1.3.14. Class I Asbestos Work:  Activities involving the removal of thermal systems insulation (TSI) and surfacing ACM and presumed asbestos containing materials (PACM).

1.3.15.  Class II Asbestos Work:  Activities involving the removal of ACM which is not TSI or surfacing material.  This includes, but is not limited to, the removal of asbestos-containing wallboard, floor tile and sheeting, roofing and siding shingles, and construction mastics.

1.3.16.  Class III Asbestos Work:  Repair and maintenance operations, where ACM, including TSI and surfacing ACM and PACM, is likely to be disturbed.

1.3.17.  Class IV Asbestos Work:  Maintenance and custodial activities during which employees contact but do not disturb ACM or PACM and activities to clean up dust, waste and debris resulting from Class I, II and III activities.

1.3.18	Clean Room:  An uncontaminated area or room which is part of the abatement worker/equipment decontamination enclosure, with provisions for storage of workers' or visitors' street clothing, protective equipment and uncontaminated materials and equipment. It may be used for changing clothes.

1.3.19	Competent Person:  In addition to the definition in 29 CFR 1926.32 (f), one who is capable of identifying existing asbestos hazards in the workplace and selecting the appropriate control strategy for asbestos exposure, who has the authority to take prompt corrective measures to eliminate them, as specified in 29 CFR 1926.32 (f).  In addition, the competent person shall have successfully completed training for Class I, Class II, Class III, and Class IV projects meeting the criteria set forth in the EPA Model Accreditation Plan (40 CFR 763) for project designer or supervisor, and operations and maintenance training.

1.3.20	Containment Barrier:  A temporary enclosure constructed with fire-retardant plastic sheeting, suitable framing, tape (as defined in 1.3.52) and other adhesives within the abatement work area.  This barrier serves to confine the asbestos abatement and decontamination work, and to contain the release of asbestos containing dust and debris through the action of pressure differential ventilation and air filtration systems.  The only entrance is via the abatement worker/equipment decontamination enclosure.

1.3.21	COTR (Contracting Officer’s Technical Representative):  An individual representing the SI as the technical advisor to the SI’s Contracting Officer.  This individual may be an employee of the SI or consultant.

1.3.22	Critical Barrier:  Those portions of the containment barrier which represent the minimum structural components necessary to maintain the asbestos removal area in airtight isolation from the surrounding areas.  Critical barriers shall be placed at floors, windows, ventilation louvers and other openings as necessary to achieve abatement work area isolation before putting up the double-layer plastic sheeting containment enclosure within which abatement work is performed.  If a temporary plastic sheeting/stud wall must be erected, it shall be treated as a critical barrier.  The double-layer plastic sheeting containment enclosure shall then be erected on that wall.  Wrappings on lights, control boxes, etc., do not constitute part of the critical barrier.

1.3.23	Curtained Doorway:  A minimum 2-flap passageway to allow access or egress from one room to another while permitting minimal air movement between the rooms of the decontamination enclosure system.  It is constructed by placing 2-3 overlapping sheets of plastic sheeting at least three feet wide over an existing or temporarily framed doorway.  The sheets shall be weighted at the bottom so that they close quickly after being released.

1.3.24	Decontamination Enclosure:  A series of connected rooms with curtained doorways between each room, for the decontamination of the abatement workers and equipment/materials.  A decontamination enclosure contains a minimum of three (3) separate rooms (typically with airlocks located between the rooms) consisting of an equipment room, shower room, and clean room.  The system is constructed of an air-tight, impermeable, temporary barrier. Framing for enclosure shall be metal or fire retardant pressure impregnated wood.

1.3.25	Disposal Bag:  A properly labeled minimum 0.15 mm thick, leak-tight plastic bag used for transporting asbestos waste from the abatement work area to an EPA-approved disposal site for ACM waste.

1.3.26	Disturbance:  Contact which releases fibers from ACM or presumed asbestos-containing material (PACM) or debris containing ACM or PACM.  This term includes activities that disrupt the matrix of ACM or PACM, render ACM or PACM friable, or generate visible debris.  Disturbance includes cutting away small amounts of ACM and PACM, no greater than the amount which can be contained in one standard sized glove bag (as defined in 1.3.29) or waste bag in order to access a building component.  In no event shall the amount of ACM or PACM so disturbed exceed that which can be contained in one glove bag or waste bag which shall not exceed 1.52 m in length and width.

1.3.27	Encapsulant:  A material applied after the removal of ACM or to the ACM-edges of partially abated substrates which surrounds or embeds residual asbestos fibers in an adhesive matrix to prevent their release into the atmosphere.  Encapsulation for purpose of final lockdown is not to be accomplished until after the project has passed final air clearance tests and the COTR has authorized removal of the containment.

1.3.28	Enclosure:  Procedures necessary to completely enclose material containing asbestos behind airtight, impermeable, permanent barriers.

1.3.29	Equipment Room:  A contaminated area or room which is part of the decontamination enclosure, with provisions for storage of contaminated clothing and equipment and cleaning supplies for decontamination of equipment.  Airlocks are required at all entrances to the equipment room.

1.3.30	EPA:  United States Environmental Protection Agency.

1.3.31  Excursion Limit:  Airborne concentration of asbestos in excess of 1.0 fiber per cubic centimeter of air (1 f/cc), as averaged over a sampling period of thirty minutes.

1.3.32	Fiber:  A particulate form of asbestos, 5 micrometers or longer, with a length-to-width ratio of at least 3 to 1.

1.3.33	Fixed Object:  A unit of equipment or furniture in the abatement work area which cannot be removed from the abatement work area.

1.3.34	Glove Bag:  A pouch, typically constructed of a minimum 0.15 mm thick, 1.5 m x 1.5 m (maximum), transparent polyethylene or polyvinylchloride plastic, with inward projecting sleeve gloves to abate ACM in a sealed micro-environment with designated inlets for amended water and sealant application, and a HEPA filtered vacuum unit attachment.  The pouch has capacity for tool storage and to hold removed ACM.

1.3.35	GFCI (Ground Fault Circuit Interrupter):  A type of ground fault protection in areas where personnel are at high risk of receiving electrical shocks (for example, in damp locations); makes use of a device designed to trip at a ground current in the milliampere range, i.e., very much below currents that are normally harmful.

1.3.36	HEPA Filter:  A High Efficiency Particulate Air (HEPA) filter capable of trapping and retaining 99.97% of all mono-dispersed particles 0.3 micrometer in diameter or larger.

1.3.37	HEPA-Filtered Vacuum Cleaner:  HEPA-filtered vacuuming equipment with a filter system capable of collecting and retaining asbestos fibers.

1.3.38	Holding Area:  A chamber between the washroom and uncontaminated area in the equipment decontamination enclosure system.

1.3.39	Impermeable Waste-Disposal Containers: Suitable to receive and retain any asbestos-containing or contaminated material until disposal at an approved site.  The containers shall be labeled in accordance with OSHA Regulation 29 CFR 1910.1001 and 29 CFR 1926.1101.  Containers must be both water-tight and air-tight.

1.3.40	Lockdown:  The process of applying encapsulant as a finishing coat to abated surfaces after project has successfully passed final air clearance tests and the COTR has authorized removal of containment.

1.3.41	Movable Object:  A unit of equipment or furniture in the abatement work area which can be removed from the abatement work area.

1.3.42	MSHA:  Mine Safety and Health Administration:

1.3.43	Negative Exposure Assessment (NEA):  A demonstration by the contractor, which complies with the criteria in OSHA 29 CFR 1926.1101(f)(2)(iii), that employee exposures during an operation are expected to be consistently below the permissible exposure limits (PELs).  Such assessment is to be used to justify level of respiratory protection to be used on the job.

1.3.44	NESHAPS:  National Emissions Standard for Hazardous Air Pollutants.

1.3.45	N.E.C.:  National Electrical Code.

1.3.46	NIOSH:  National Institute for Occupational Safety and Health.

1.3.47	OSHA:  Occupational Safety and Health Administration.

1.3.48	PACM:  Presumed Asbestos-Containing Material, meaning thermal system insulation and surfacing material found in buildings constructed no later than 1980.

1.3.49	PEL:  Permissible Exposure Limit.  An occupational limit of exposure to a chemical substance or physical agent.

1.3.50	Personal Monitoring:  Sampling of asbestos fiber concentrations within the breathing zone of an employee.  Breathing zone is defined as a radius of 150 mm to 250 mm around the employee's head.

1.3.51	Personal Protective Equipment:  Equipment which may consist of coveralls, shoes, gloves, helmet, goggles, and respirator used for protection against asbestos exposure.

1.3.52	Plastic Sheeting:  Fire retardant Polyethylene sheet material of specified thickness used for protection of walls, floors, etc., and critical barriers in the abatement work area.

1.3.53	Protection Factor:  The ratio of the ambient concentration of an airborne substance to the concentration of the substance inside the respirator at the breathing zone of the wearer.  The protection factor is a measure of the degree of protection provided by a respirator to the wearer.

1.3.54	Respirator:  A device designed to protect the wearer from the inhalation of harmful atmospheres and approved by NIOSH or MSHA for a specific category of use.

1.3.55	SI IH - Smithsonian Institution’s Industrial Hygienist:  An individual serving as the Smithsonian’s industrial hygienist.  This individual may be an employee or consultant.

1.3.56	Surfactant:  A chemical wetting agent added to water to decrease surface tension and improve material penetration.

1.3.57	Tape:  Glass fiber or other tape capable of sealing joints of adjacent sheets of plastic (0.15 mm polyethylene) and for attachment of plastic sheets to finished or unfinished surfaces of dissimilar materials under both dry and wet conditions, including use of amended water.  Minimum tape width shall be 51 mm.

1.3.58	Warning Labels and Signs:  As required by OSHA regulations 29 CFR 1910.1001 and 1926.58.

1.3.59	Waste Water Filters:  Discharged liquids shall pass through a primary filter and the output shall be particles 20 microns or smaller.  The secondary filter shall have output particles 5 microns or smaller.

1.3.60	Wet Cleaning:  The process of eliminating asbestos contamination from building surfaces and objects by using cloths, mops, or other cleaning tools which have been dampened with amended water.

1.4	Regulations and References

1.4.1	Regulations:  Contractor shall comply with the most current edition of all federal, state, county, and city codes and ordinances as they apply to the location(s) in which the work is performed.  Make available for review at the site one copy of all applicable federal, state, county and city regulations governing the abatement work, including but not limited to:

1.4.1.1		Occupational Safety and Health Administration (OSHA), U.S. Department of Labor

(a)		29 CFR 1910 (General Industry) and 29 CFR 1926 (Construction) Occupational Safety and Health Standards

(b)		29 CFR 1910.1001 and 29 CFR 1926.1101 Asbestos

(c)		29 CFR 1910.134  Respiratory Protection

(d)		29 CFR 1910.1200  Hazard Communication

1.4.1.2			U. S. Department of Transportation

(a)		49 CFR 171 Subchapter C, Hazardous Materials Regulations

(b)		49 CFR 172 Subchapter C, Shipping Container Specifications

1.4.1.3	U.S. Environmental Protection Agency

(a)	40 CFR 763, Toxic Substances Control Act; particularly Subpart E, Asbestos Containing Materials in Schools

(b)	40 CFR 61, Sub-parts A and M, National Emission Standard for Hazardous Air Pollutants (NESHAPS)

1.4.1.4		District of Columbia Law Title 20 DCMR Section 800.  District of Columbia Department of Health.

1.4.1.5		New York City Department of Environmental Protection.

1.4.1.6		New York State Department of Health; New York State Department of Environmental Conservation; New York State Department of Labor.

1.4.1.7		Virginia Department of Labor and Industry; Virginia Department of Professional and Occupational Regulation; Virginia Department of Environmental Quality.

1.4.1.8		Maryland Department of the Environment; Maryland Occupational Safety and Health.

1.4.1.9		Arizona Department of Environmental Quality.

1.4.1.10	Hawaii Department of Health.

1.4.1.11	Florida Department of Environmental Protection.

1.4.1.12	Massachusetts Department of Environmental Protection.

1.4.1.13	American National Standards Institute (ANSI), 1430 Broadway, New York, New York  10018. Telephone (212)354-3300

(a)		ANSI Publication Z88.2 Practices for Respiratory Protection

1.4.1.14		American Society for Testing and Materials (ASTM), 1916 Race Street, Philadelphia, PA 19103. Telephone (215) 299-5400

(a)		ASTM Standard P-189 Specification for Encapsulants for Friable Asbestos Containing Building Materials Proposal

1.4.1.15		Compressed Gas Association, Inc.  New York.  Pamphlet G-7 "Compressed Air for Human Respiration", Specification G-7.1 Commodity Specification for Air"

1.4.1.16		Canadian Standard Association (CSA), Rexdal, Ontario, Standard Z180.1, "Compressed Breathing Air".

1.5	Submittals

1.5.1	Reference Division 1, Section 01000 Supplementary Conditions for Construction, for additional requirements.

1.5.2	Contractor's Work Plan:  The Contractor shall submit a Contractor's Work Plan for asbestos abatement work within 15 calendar days after contract award to the COTR for approval.  Approval of the Plan is required prior to beginning abatement work.  The Plan shall be on 220 mm x 280 mm paper in a binder indexed by the subjects listed below.  Detail the procedures, instructions, and reports used to assure compliance with the contract documents.

1.5.2.1			Barchart Schedule:  Provide barchart scheduling of the abatement work by daily and/or weekly increments for each abatement work area and individual decontamination enclosure system.  The time line is to include all work, both on and off the job site, for the entire contract period.

1.5.2.2			Notices:  The contractor shall notify federal, state, and local regulatory agencies in writing immediately upon contract award and a minimum of 10 days in advance of any asbestos related work.  Notifications shall be made by the Contractor as required by USEPA National Emission Standards for Hazardous Air Pollutants (NESHAPS) Asbestos Regulations (40 CFR 61, Subpart M)). Submit copies of notifications and documentation to the COTR.  If a project consists of multi-phases, with distinct start and stop dates, these shall be declared on the EPA Notice or individual notices shall be filed for each phase.

1.5.2.3			Permits and Licenses:  Maintain current licenses and obtain applicable permits as required by federal and applicable state or local jurisdictions for the removal, transporting, disposal or other regulated activity relative to the abatement work of this contract.  Submit copies of all state and local licenses and permits necessary to carry out the abatement work of this contract.

(a)	All asbestos containing waste is to be transported by an entity maintaining a current "Industrial waste hauler permit" specifically for asbestos-containing materials, as required for transporting of waste asbestos-containing materials to a disposal site.

(b)	Notices of Violations:  Submit copies of all Notices of Violations issued to the contractor and its sub-contractors within the last three (3) years by federal, state, and local regulatory agencies.

1.5.2.4			Sequence of Work:  Narrative description of the proposed sequencing of asbestos work and breakdown of abatement work areas requiring separate or individual decontamination enclosures. Include how enclosure systems will be erected and dismantled.  Include how re-useable equipment will be cleaned for re-use before relocation or removal from the site.  Include how waste disposal containers will be cleaned and removed from the abatement work area.

1.5.2.5			Abatement Work Area Layout Sketch: Layout sketch of decontamination enclosure systems and abatement work area.  Describe assembly of construction, materials to be used and location of notices to be posted on the job site.  Indicate which areas will be sealed off (and by what means). Show locations of facilities and equipment such as showers, lockers, storage, etc.  Show locations of all filtration devices to be used, their exhaust, and calculations to determine the number of these devices needed to provide the minimum 4 air changes per hour in the abatement work area.  These requirements shall be coordinated with the COTR and facility representative

1.5.2.6			Isolation of Abatement Work Areas: Methods to isolate/restrict access to abatement work areas.  Include how access will be controlled, how building HVAC ventilation systems will be isolated from abatement area.  Include how security and fire systems will be maintained within the containment.  Include plans for electrical lock-out and dedicated electrical systems.  These requirements shall be coordinated with the COTR and facility representatives.

1.5.2.7			Transportation and Disposal:  Details of hauling equipment, materials and contaminated debris from inside the building.  Submit written identification of licensed hauler and landfill location.

1.5.2.8			Personnel Organization and Responsibilities:  The Contractor shall provide a list of all project personnel, both on-site and in the offices, and a statement of their responsibilities and authority for work on this project.

1.5.2.9			Personal Protective Equipment:  Details of personal protective equipment and use, storage and maintenance at job site.

1.5.2.10		Posted Notices and Warning Signs:  Submit copies of notices to be posted at the job site, as required by EPA and OSHA regulation for asbestos abatement activities.

1.5.2.11		Materials and Equipment Product Data: Submit manufacturer's literature and written information for all materials and equipment, including NFPA test report of flame resistant materials, and material safety data sheets for all chemical-content supplies.  Contractor shall not change materials or equipment without approval of a new submittal to the COTR.

1.5.2.12		Contractor Monitoring Services:  Before start of asbestos work, submit to the COTR the name of the contractor's industrial hygiene consultant and analytical laboratory for air monitoring.

1.5.2.13		Superintendent/Competent Person:  Before start of asbestos work, submit to the COTR the name of job site supervisor who must meet the following requirements as a minimum.  Furnish documentation that the General Superintendent:

(a)		has a minimum of five (5) years on-the-job experience as a supervisor of asbestos abatement projects

(b)		 is a competent per Section 1.3.15 of this document.

(c)		is certified as an Asbestos Abatement Supervisor in accordance with 40 CFR Part 763.

(d)		is fluent in the English language and all other primary languages spoken by the abatement work crew.

1.5.2.14		Workers' Specialized Training:  Submit training course descriptions, locations, and dates. Submit to the COTR a written affidavit before start of asbestos removal as proof that all employees have had instruction on the hazards of asbestos exposure; and on all aspects of work procedures and personal protection and area protective measures as required and/or recommended by OSHA and EPA and other applicable guide documents.  The affidavit shall include course name, designation, installation, place, date taken, and student names.

(a)		Training shall be in accordance with 29 CFR 1926.1101.

(b)		Course certification shall be in accordance with EPA as required by 40 CFR 763.

(c)		Workers should have a minimum of one (1) year experience as an asbestos worker.

1.5.2.15		Respiratory Program:  Submit a written respiratory program as defined in OSHA 1926.1101 and in these specifications.  Submit type of NIOSH/MSHA certified respiratory equipment intended for each operation required by this project. Selection criteria must meet 29 CFR 1926.1101 (h) (2).  When a Type "C" supplied positive pressure air respiratory system is required by the abatement work, submit drawing showing assembly of components into a complete supplied air respiratory system. Include diagram showing location of compressor, filter banks, backup air supply tanks, hose line connections in abatement work area(s), routing of air lines to abatement work area(s) from compressor.

1.5.2.16		Negative exposure assessment data submitted to justify respiratory selection must be less than 12 months old and closely resemble the current project following criteria set forth in 29 CFR 1926.1101 (f) (2) (iii).

1.5.2.17		Emergency Preparedness:  Submit an emergency plan to COTR for approval by SI  Office of Safety, Health and Environmental Management (OSHEM). The emergency plan shall address responses to fire, accident, power failure, pressure differential system failure, supplied air system failure, or any other event that may requiremodification or abridgement of decontamination or abatement work area isolation procedures.  Show exit routes from the building, locations of the nearest manual pull stations, telephone number of Smithsonian security office, name of the designated employee responsible for fire protection, fire hazards inherent to the project and measures taken for prevention.  All employees shall be familiar with the emergency plan and have initialed the plan after reading it, know how to activate the fire alarm, and trained in the use of portable fire extinguishers.  One on-site employee shall be designated as responsible for fire protection. The plan shall be available at the job site in all primary languages of the abatement work crew.  In addition, the following emergency information shall be posted at all entrances to the abatement work area:

(a)		Exit route map

(b)		Phone number of SI security office

1.6	Daily Reports

1.6.1	The Contractor shall correspond with the COTR for all matters related to this construction project, unless otherwise directed.

1.6.2	All correspondence with the SI shall be in the English language, signed and dated by the Contractor.

1.6.3	Reference General Conditions (Construction Contract Clauses) and Specifications Division 1 for Supplementary Conditions for Construction.

1.6.4	The Contractor shall maintain daily logs and reports of job-site activities and personnel exposure monitoring at the site and shall provide copies to the COTR for inspection upon request.

1.6.5	The Contractor shall maintain daily reports using the SI Contractor’s Daily Report form.  Reports shall be numbered consecutively and all sections shall be completed or noted as ‘not applicable.’  Each day’s report shall contain detailed remarks including but not limited to progress on the job, problems discovered, and discussions with Smithsonian staff.  Reports shall be submitted to the COTR each day for the previous work day.. Copies shall be maintained at the jobsite and made available to the COTR upon request.

1.6.6	Reporting Unusual Events:  When an event of unusual and significant nature occurs at site (examples: failure of pressure differential system, rupture of temporary enclosures, equipment or power failure, high airborne fiber reading), prepare and submit a special report listing chain of events, persons participating, response by Contractor's personnel, evaluation of results or effects, and similar pertinent information.

1.6.7	Accident Reporting:  Report all accidents to Smithsonian Security Office first, then to the COTR. Prepare reports of significant accidents, at site and anywhere else work is in progress.  Record and document data and actions; comply with industry standards.  For this purpose, a significant accident is defined to include events where personal injury is sustained, property loss of substance is sustained, or where the event posed a significant threat of loss or personal injury.  Report shall be submitted to the COTR, who will forward copies to OSHEM and the facility Safety Coordinator.

1.6.8	Waste Manifest-Asbestos:  At completion of hauling and disposal of each load, submit a copy of waste manifest, chain of custody form, and landfill receipt to the COTR.  Waste manifest to be submitted shall be signed by the contractor, waste transporter, and the disposal facility.  A copy of all manifests will be included in the post-job submittal.

1.6.9	Waste Manifest-Hazardous Waste:  Any hazardous waste generated as a result of asbestos abatement activities will be disposed of by a Certified Hazardous Waste Disposal Contractor.  A copy of the Hazardous Waste Manifest generated by this disposal is to be submitted to the COTR, who will forward a copy to the facility’s SI Hazardous Waste Coordinator.  A copy of all manifests will be included in the post-job submittal.

1.7	Product Handling

1.7.1	Deliver all materials in  the original packages, containers, or bundles bearing the name of the manufacturer and the brand name.

1.7.2	Store all materials subject to damage off the ground, away from wet  or damp surfaces, and under cover sufficient to prevent damage or contamination.

1.7.3	Remove from the premises all damaged or deteriorated materials.  Dispose of materials that become contaminated with asbestos in accordance with applicable regulatory standards and these

specifications.

PART 2 - PRODUCTS

2.1	Materials

2.1.1	Caulking:  High-grade rubber base caulk for masonry and/or for other materials.

2.1.2	Encapsulant:  Product shall be rated as acceptable for use intended when field tested in accordance with ASTM Proposed Specification P-189 “Specification for Encapsulants for Friable Asbestos Containing Building Materials".  Use only materials that have a flame spread index of 25 or less when dry, when tested in accordance with  ASTM E-84.

2.1.3	Glove-Bag:  0.15 mm thick, 1500 mm x 1500 mm, transparent polyethylene or polyvinylchloride plastic with long sleeve gloves, designated inlets for HEPA vacuum attachment, and storage pouch.

2.1.4	Impermeable Waste-Disposal Containers: Suitable to receive and retain any asbestos-containing or contaminated material until disposal at an approved site.  The containers shall be labeled in accordance with OSHA Regulation 29 CFR 1910.1001 and 29 CFR 1926.1101.  Containers must be both water-tight and air-tight.

2.1.5	Plastic Sheeting:  Product Standard PS 17-69 and OSHA Regulation 29 CFR 1926.1101; Polyethylene plastic sheeting material 0.15 mm thickness for covering floors and walls, providing air locks, and sealing doors and windows; supply in appropriate widths to minimize seams. Must be flame-resistant material and must meet test criteria in NFPA 701.  Reinforced sheeting is required for applications subject to wear and tear.

2.1.6	Surfactant (Wetting Agent):  50% polyoxyethylene ester and 50% polyoxyethylene ether, or approved equal, shall be mixed with water to provide a concentration of 2 ml surfactant to 1 liters of water, or manufacturer's recommended concentration.

2.1.7	Tape:  Glass fiber or other tape capable of sealing joints of adjacent sheets of plastic sheeting and for attachment of plastic sheets to finished or unfinished surfaces of dissimilar materials under both dry and wet conditions, including use of amended water.  Minimum tape width shall be 50 mm.

2.1.8	Warning Labels and Signs:  As required by OSHA regulations 29 CFR 1910.1001 and 1926.58.

2.1.9	Waste Water Filters:  Discharged liquids shall pass through a primary filter and the output shall be particles 20 microns or smaller.  The secondary filter shall have output particles 5 microns or smaller.

2.2	Equipment

2.2.1	Air Filtration Units:  Shall be factory-sealed and equipped with HEPA filters(final), pre-filters, instrumentation to monitor pressure differential, and safety and warning devices.

2.2.1.1			Provide units with electrical components approved by the National Electrical Manufacturers Association (NEMA) and Underwriter's Laboratories (UL).

2.2.1.2			Access to the units for replacement of all air filters shall be from intake end.  Provide units with pre-filters and intermediate filters installed either on or in the intake grid of the unit and held in place with special housings or clamps.  The filter media shall be completely sealed on all edges with a structurally rigid frame with a continuous rubber gasket.

2.2.1.3			HEPA Filters:  Provide units equipped with HEPA filters.  Filters shall be individually tested and certified by the manufacturer.

2.2.1.4			Pre-filters:  Provide a two-stage pre-filtration to extend the life of the primary HEPA filter.  The first-stage pre-filter is a low-efficiency type effective for particles 100 micrometers and larger.  The second-stage (or intermediate) filter has a medium efficiency effective for particles down to 5 micrometers.

2.2.1.5			Instrumentation:  Provide units equipped with a magnehelic gauge or manometer to measure the pressure drop across filters and to indicate when filters have become loaded and need to be changed. A table indicating the usable air-handling capacity for various static pressure readings on the magnehelic gauge affixed near the gauge for reference, or the magnehelic reading indicating at what point the filters should be changed, noting cubic feet per minute (CFM) air delivery at that point.  Provide an elapsed time meter to show the total accumulated hours of operation.

2.2.1.6			Safety and Warning Devices:  Provide units with the following safety and warning devices:

(a)		Warning lights to indicate normal operation, too high a pressure drop across the filters (i.e., filter overloading), and too low of a pressure drop (i.e., rupture in HEPA filter or obstructed discharge)

(b)		GFCIs.

(c)		Audible alarm if unit shuts down due to operation of safety systems.

(d)		Electrical overload protection sized for the equipment.  The motor, fan, fan housing, and cabinet are to be grounded.

2.2.2	Respirators and Respirator Systems

2.2.2.1			Product Data:  Must possess NIOSH and MSHA approval for each component in an assembly and/or for entire assembly.

PART 3 - EXECUTION

3.1	Controlled Access to Site

3.1.1	Access to the abatement work area shall be restricted to contractor's workers and authorized visitors as defined in these specifications.

3.1.2	Authorized visitors shall have access to the work site at all times following notification to COTR. Contractor shall supply protective clothing and equipment for visitors as necessary, except for respirators which are to be  provided by the visitor in accordance with Section 3.4 of this document.

3.1.3	Contractor shall prominently post signs at all potential entry points to the abatement work area which clearly state:  "Restricted Area Under Construction-Admittance by Special Permission Only - Protective Clothing Required Beyond This Point".  Immediately inside entry point and outside critical barriers post a warning sign meeting specifications of OSHA 29 CFR 1910 and 1926.  Suggested format is a sign of minimum size 508 mm by 356 mm displaying the following legend:

==============================================

DANGER

ASBESTOS

CANCER AND LUNG DISEASE HAZARD

AUTHORIZED PERSONNEL ONLY

RESPIRATORS AND PROTECTIVE CLOTHING ARE

REQUIRED IN THIS AREA

=============================================

3.1.4	All workers and authorized visitors shall enter the abatement work area only through the abatement worker/equipment decontamination enclosure, in accordance with Section 3.3 of this document.

3.1.5	All workers and authorized visitors, before entering the abatement work area, shall read and be familiar with all posted regulations, personal protection requirements, and emergency procedures and exit routes.

3.1.6	Contractor shall maintain a daily job site personnel log listing names and social security numbers of individuals who entered the abatement work area, and the times of entering and leaving the area.

3.2	Worker and Visitor Protection

3.2.1	No eating, drinking, smoking, or chewing gum is permitted within the abatement work area.  The COTR shall designate a "break area" where these activities, except for smoking, are permitted.  Smoking is prohibited in SI facilities.

3.2.2	Workers and Visitors shall be fully protected with respirators and protective clothing during any work which may disturb asbestos-containing materials and result in fiber release.  Full protection is not required during pre-abatement inspections of the containment, while work is not being conducted.

3.2.3	Protective Clothing and Equipment:  Provide workers and visitors with sufficient sets of protective full body clothing, to include full body coveralls with hood, boots (for workers) and footwear coverings (for workers and visitors), and gloves.  Provide eye protection and hard hats as required by applicable safety regulations.  Contaminated non-disposal clothing and footwear shall be left in the equipment room until the end of the asbestos abatement work, at which time such items shall be disposed of as asbestos waste, or shall be thoroughly cleaned of all asbestos or asbestos-containing material.  Contractor shall have at least six (6) sets of disposable protective full body clothing for COTR and authorized visitors for each work day.  Provide storage facilities for visitors and workers for removed street clothing in the clean room.

3.2.3.1			Boots:  Provide workers non-skid type work boots with protective shields as required by OSHA.  Paint uppers of boots with red waterproof enamel paint as a permanent marking that the boots have been exposed to ACM abatement work areas.  These boots are to be handled as asbestos-contaminated materials.

3.2.3.2			Hard Hats:  Provide hard hats that meet ANSI Z89.1 for use where work is overhead, scaffolding is being used, or as otherwise required by OSHA.  Label hats with same warning labels as required for ACM disposal bags.

3.2.3.3			Goggles:  Provide goggles that meet ANSI Z87.1 as required by OSHA.

3.2.3.4			Gloves:  Provide disposable work gloves for use in the abatement work area.

3.2.3.5			Coveralls with Hood:  Provide disposable coveralls with hoods for use in the abatement work area.

3.2.3.6			Respirators:  Provide workers with personally issued and marked respirator equipment approved by NIOSH/MSHA and, in accordance with these specifications, suitable for the asbestos exposure level in the abatement work area.  Where respirators with disposable filters are employed, provide sufficient filters for replacement as necessary by the abatement worker, or as required by the applicable regulation.  Authorized visitors must provide their own respirators, with fresh filters or cartridges as necessary, to enter the abatement work area.  These are minimum requirements.  Section 3.4 of this document is to be consulted for more detail.

3.3	Abatement Work Area Entry and Exit Procedures

3.3.1.	Each time the abatement work area is entered remove all street clothes in the Clean Room of the Decontamination Enclosure and put on new disposable coveralls, new head cover, and a clean respirator. Proceed through shower room to equipment room and put on work boots.

3.3.2	Each time the abatement work area is exited, the following procedures shall be followed:

3.3.2.1			Before leaving the regulated area, employees and authorized visitors shall remove all gross contamination and debris from their protective clothing.

3.3.2.2.		Personnel exiting the regulated area shall remove their protective clothing and equipment (except respirators) in the equipment room and deposit the clothing in labeled impermeable bags or containers.

3.3.2.3			Personnel shall remove their respirators in the shower room, washing and rinsing them.

3.3.2.4			Personnel shall shower thoroughly before entering the clean room.

3.3.2.5			After showering, employees shall enter the clean room before changing into street clothes.

3.4	Respiratory Protection

3.4.1	Contractor is hereby advised that asbestos has been determined by the U.S. Government to be a CANCER-CAUSING AGENT.  Provide workers with respirators [which, as a minimum, meet the requirements of OSHA 29 CFR 1926.1101] and protective clothing during all phases of the abatement work and until final air tests are accepted by COTR.

3.4.2	The Contractor shall select respirators from among those jointly approved as being acceptable for protection by the MSHA and the NIOSH under the provisions of 30 CFR Part 11.

3.4.3	The Contractor shall select and provide respirators, at no cost to the employee and shall ensure that the employee uses the respirator provided.

3.4.4	Instruct and train each worker involved in asbestos abatement or maintenance and repair of asbestos-containing materials in proper respiratory use and require that each worker always wear in the abatement work area a respirator, properly fitted on the face.  The respirator shall be worn from the start of any operation which may cause airborne asbestos fibers until the abatement work area is completely decontaminated.

3.4.5	Allow an individual to use only those respirators for which training and fit-testing have been provided.  Require that each time an air-purifying respirator is put on it be checked for fit with a positive and negative pressure fit test in accordance with the manufacturer's instructions or ANSI Z88.2.

3.4.6	For all jobs that involve the removal of thermal system insulation (TSI) or surfacing materials (OSHA definition of Class I work) the employer shall provide respirator protection in accordance with 29 CFR 1926.1101 (h) Table 1 - Respiratory Protection for Asbestos Fibers.  This level of respiratory protection shall be maintained until the employer can produce a negative exposure assessment.

3.4.7	For all other abatement work, use respiratory protection appropriate for the fiber level encountered in the abatement work area or as required for other toxic or oxygen-deficient situations encountered.  The level of respiratory protection which supplies an airborne fiber level inside the respirator, at the breathing zone of the wearer, at or below the permissible exposure limit (PEL) is the minimum level of protection allowed.  (Table

1, Respiratory Protection for Asbestos Fibers, 29 CFR 1926.1101)  Do not use single-use, disposable, or quarter-face respirators.

3.4.8	Authorized visitors are responsible for providing their own respirator and replacement filters and cartridges, with the exception of Type C which shall be provided by Contractor, and for having been previously and properly trained fit-tested, for the respirator used.

3.4.9	For use with air-purifying respirators, provide, at a minimum, HEPA type filters certified by NIOSH and MSHA for protection against asbestos fibers. In addition, a chemical cartridge may be added, if required for protection against chemicals used on this job.

3.4.10	For use with powered air purifying respirators, supply a sufficient quantity of HEPA filters approved for asbestos, so workers can change filters at any time that flow through the face piece decreases to the level at which the manufacturer recommends filter replacement.

3.4.11	For supplied-air respirator systems, provide equipment capable of producing air used for breathing in Type "C" supplied air respiratory systems that meets or exceeds standards set for C.G.A. Type 1, Gaseous Air, Grade D. (See 1.5.2.15)  System must be certified by NIOSH/MSHA as an approved Type "C" respirator assembly operating in pressure demand mode with a positive pressure face-piece including as a minimum the following:

- Auxiliary backup system

- Escape air supply

- Backup air supply

- Warning Alarm Device

- Compressor Shut Down

- Compressor Motor (electric)

- Compressor Location (outside building)

- Air Intake

- After-Cooler

3.5	Air Monitoring; Stop Action and Clearance Levels

3.5.1	This section describes work being performed by the SI.  The SI will not be performing air monitoring to meet Contractor's OSHA requirements for personal sampling or any other purpose..  The Contractor is to conduct air monitoring required by OSHA for Contractor personnel.

3.5.2	Analytical Methods:  The following methods will be used by the SI in analyzing filters used to collect air samples.  Minimum sample volumes will be 1200 liters for clearance samples.

3.5.2.1			Phase Contrast Microscopy (PCM) - will be performed using the OSHA Reference Method, Appendix A to 29 CFR 1926.1101, or NIOSH Method 7400.

3.5.2.2			Transmission Electron Microscopy (TEM) - will be performed using the analysis method set forth in the AHERA regulation 40 CFR Part 763 Appendix A, or NIOSH Method 7402, whichever is deemed more appropriate by SI in each  case.

3.5.3	Before Start of Work:  The SI will secure abatement work area air samples to establish a base line fiber level in each homogeneous abatement work area before start of work.  All samples will be taken at the same time to ensure identical environmental conditions.

3.5.4	Daily:  From start of abatement work through project decontamination, the SI may be taking samples on a daily basis inside and outside each abatement work area.

3.5.5	All Clearance Air Samples will be taken using aggressive sampling techniques.

3.5.6	Stop Action:  If any air sample taken outside of the abatement work area exceeds 0.01 f/cc by PCM, or 70 structures per mm2 by TEM, depending on sampling method used, immediately and automatically stop all work except corrective action.  PCM air samples will be re-analyzed by TEM to determine whether the high outside-of-work-area results were due to asbestos or non-asbestos fibers. The SI and the abatement contractor will determine the source of the high reading.  The contractor will correct the condition, as appropriate.

3.5.7	Abatement Work Area Final Clearance Levels:

3.5.7.1	The SI standard for abatement work area final clearance in all occupied areas for removing the containment and re-occupancy is 70 structures per mm2 by TEM using the analysis method set forth in the AHERA regulation 40 CFR Part 763 Appendix A.

3.5.7.2  The SI standard for abatement work area final clearance in un-occupied areas, or at the case-by-case discretion of the SI, is less than 0.01 fibers per cubic centimeter of air using PCM methods specified in NIOSH 7400.

3.5.7.3 	Final air clearance requirements of specific state and local regulations that exceed the requirements of 3.5.7.1 and 3.5.7.2 will be utilized (e.g., in the District of Columbia, at least two PCM samples per 2,500 square feet of floor are required).

3.6	Initial Isolation of Abatement Work Area

3.6.1	Contractor shall completely separate the abatement work area from other portions of the building, and the outside, by sealing all openings (windows, doorways, elevator openings, corridor entrances, drains, ducts, grill, diffusers, skylights, etc.) with barriers of 0.15 mm polyethylene sheeting and tape, or by sealing cracks leading out of the abatement work area. Contractor shall caulk the joints and seal holes in that portion of the walls, ceiling, and floor inside the abatement work area that could allow airborne asbestos fibers to be carried into adjoining spaces, or the exterior.  Note in particular where pipes, conduit, and ductwork penetrate walls, ceilings and floor.  Doorways and corridors which will not be used for passage during work must be sealed with 9.5 mm plywood, wood framing and plastic sheeting with tape.

3.6.2	All heating, ventilating, and air conditioning (HVAC) components that are in, supply or pass through the abatement work area shall be shut down.  During asbestos removal and until job completion, elevators, exhaust fans, and HVAC vents and intakes will be key locked to not operate in the abatement work area.

Coordinate with the COTR and Building Representative which areas are to be shut down and for what duration.  Seal all intake and exhaust vents, and seams in system components, with a double layer of 0.15 mm polyethylene sheeting.

3.6.3	If it becomes necessary to shut down electric power to the enclosed abatement work area, then the contractor shall provide temporary power and lighting and ensure safe installation of temporary power sources and equipment in accordance with NFPA 70 electric code requirements.

3.6.4	Arrange for the abatement work area to be locked during non-work hours.  Install temporary doors with entrance type locksets that are key lockable from the outside and always unlocked and operable from the inside.  Remove deadbolts and padlocks.  Provide one key (to be held by SI security office on site) to the COTR.

3.7	Preparation of Abatement Work Area and Temporary Enclosures

3.7.1	No exhibit collection object shall be handled by the contractor without the approval of the COTR. Methods for surface decontamination and/or disposal of unsalvageable objects shall be determined with the input from the COTR, the object owner, the contractor and the SI IH.

3.7.2	Clean all contaminated furniture, equipment, and supplies with a HEPA-filtered vacuum cleaner or by wet wiping, as directed by the COTR, prior to being moved or covered.

3.7.3	Before removal, clean by HEPA-filtered cleaner and/or by wet wiping, all electrical and mechanical items, (such as lighting fixtures, clocks, diffusers, registers, etc.) and general construction items (such as cabinets casework, door and window trim, moldings, etc.) which cover the surface of the abatement work as required to prevent interference with the abatement work.  Reinstall all such materials upon completion of the removal work with materials, finishes, and workmanship to match existing installations before start of work.

3.7.4	Remove all removable furniture, equipment, and supplies that have been deemed by the COTR to be uncontaminated, or completely cover with 2 layers of polyethylene sheeting, at least 0.15 mm in thickness, securely taped in place with duct tape.  Such furniture, equipment, and supplies shall be considered outside the abatement work area unless covering plastic or seal is breached.

3.7.5	Clean all surfaces in abatement work area with a HEPA-filtered vacuum cleaner or by wet methods prior to installation of primary barrier.

3.7.6	All critical barriers, including ventilation openings (supply and exhaust), lighting fixtures, clocks, doorways, windows, speakers, and other openings into the abatement work area shall be individually sealed with 0.15 mm plastic sheeting and tape.  Elevator doors, fire extinguisher cabinets and all other penetration in the floor, walls, or ceiling shall be sealed in the abatement work area.  If a temporary polyethylene/stud wall must be erected, that wall shall be treated as a critical barrier.  The double layer polyethylene containment enclosure shall then be erected on that wall.  Critical barriers shall be sealed prior to installation of primary barriers

3.7.7	Take care in sealing of lighting fixtures and control boxes to avoid melting or burning of sheeting. The inside of unsealed lighting fixtures, control boxes, and buss lines are to be cleaned by asbestos workers specially certified to work on high voltage lines.

3.7.8	Cover floor of  abatement work area with 2 layers of clear polyethylene, at least 0.15 mm in thickness, turned up at the walls at least 600 mm.  Both spray-glue and duct tape all seams in floor covering. Size to minimize seams.  Locate seams in top layer 2.0 meters from, or at right angles to, seams in bottom layer.  Install sheeting so that top layer can be removed independently of bottom layer.  Do not locate seams at wall/floor interface.

3.7.9	If carpeting is to remain, cover carpeting with three layers of polyethylene sheeting at least 0.15 mm in thickness.  Place one layer of corrugated cardboard sheets between the top and middle layers of polyethylene.

3.7.10	Cover plastic sheeting in areas where scaffolding is to be used with a single layer of 12.7 mm fire retardant plywood.  Wrap edges and corners of each sheet with duct tape.

3.7.11	Cover all walls in abatement work area including critical barrier sheet plastic with primary barrier of 2 layers of 0.15 mm polyethylene sheeting, mechanically supported and sealed with duct tape or spray-glue in the same manner as critical barrier sheet plastic.  Size to minimize seams.  Seams shall be staggered and separated by at least 600 mm.  Wall sheeting shall overlap floor sheeting by at least 406 mm beyond wall/floor joint.  Tape all joints including the joining with the floor covering with duct tape or as otherwise indicated by the COTR.

3.7.12	Cover interior surfaces of any existing elevator with 2 layers of 0.15 mm plastic sheeting.  Arrange entry to abatement work area so that elevator door is in a positively pressurized space outside the clean room of the decon unit.

3.7.13	When installing the critical and primary barriers, automatic sprinkler heads and fire detectors shall not be covered or altered to prevent or delay operation.  Smoke detectors should be protected (but not completely masked) to avoid nuisance alarms during paint or demolition operations.  The covers on the smoke detectors shall be removed directly after such operations and at the end of the abatement workday.

3.7.14	A secondary barrier of plastic as a drop cloth shall be used to protect the primary layer from debris and shall be rolled and disposed as contaminated waste at the end of each workday.

3.7.15	 Provide emergency exiting from the enclosure as required by NFPA 101, Life Safety Code.  Arrange exit door(s) so that it is secure from outside the abatement work area but permits exiting from the abatement work area.  Mark outline of door on barriers with luminescent paint at least 250 mm wide.  Hang a razor knife on a string beside outline.  Post a sign identifying "EMERGENCY EXIT", using letters at least 150 mm high, inside outline with luminescent paint.  Arrows shall be taped on the polyethylene wall covering at eye level and at floor level to indicate location of exits.  At entrance to decontamination chamber, post building floor plan and escape routes, plus locations of nearest exist and phone numbers of SI security.  Emergency lighting shall be required, in accordance with the Life Safety Code.

3.7.16	A 4.5 kg ABC type portable fire extinguisher shall be located by each exit and clean room.

3.7.17	Install inspection windows in the containment barrier enclosure system walls.  Each window shall have a minimum 600 mm x 600 mm viewing area fabricated from 6.0 mm acrylic or polycarbonate sheeting.  Install window with top at 2.0 m above floor height in a manner that provides unobstructed vision from outside to inside of the abatement work area.  A sufficient number of windows are to be installed to provide observation of all portions of the abatement work area that can be made visible from adjacent areas.  Provide also for viewing to be blocked from the inside with opaque plastic flap.

3.7.18	Where the abatement work area is immediately adjacent to or within view of occupied areas, provide a visual barrier of opaque polyethylene sheeting at least 0.15 mm in thickness so that the abatement work procedures are not visible to building occupants.  Where this visual barrier would block natural light, substitute frosted or woven rip-stop sheet plastic in locations approved by the COTR.

3.7.19	Provide GFCI protection for all electrical equipment.

3.7.20	Provide temporary lighting inside the decontamination enclosure facility.

3.8	Construction of Worker/Equipment Decontamination and Waste Load-Out Enclosures

3.8.1	Worker/equipment decontamination enclosures shall be provided at each location where workers shall enter or exit the abatement work area.

3.8.2	The Contractor shall construct a worker/equipment decontamination enclosure consisting of at least a clean room, a shower room, and an equipment room, each separated by 900 mm air locks. Narrower air locks may be built if approved by the COTR.

3.8.2.1			All rooms shall be constructed of or fully lined with 0.15 mm thick polyethylene sheeting and suitable framing to make them as air-tight as possible. Where joining separate sheets of polyethylene is necessary, the two sheets of polyethylene shall be over-lapped at least 150 mm and adhered with an unbroken line of tape in such a manner to prohibit air movement.  Stagger joints. Tape shall then be used to further seal the joint on the other side of the containment barrier so that both loose edges of the overlap are completely sealed.

3.8.2.2			Doorways will consist of three 3 sheets of 0.15 mm polyethylene from ceiling to floor.  The width of these polyethylene sheets shall be sufficient to prevent air movement through the doorways when closed.

These doorways shall be the only source of make-up air for the HEPA negative air filtration unit under normal circumstances, unless other sources are specifically approved by the COTR.

3.8.2.3			Provide GFCI protection for all electrical equipment.

3.8.2.4			Provide temporary lighting inside the decontamination enclosure facility.

3.8.3	The Clean Room shall have a curtained doorway leading to the outside of the abatement work area, and an airlock leading to the Shower Room.  The clean room shall be of sufficient size to accommodate at least one worker, and a supply of clean disposable coveralls and storage facilities for street clothing, and uncontaminated equipment.

3.8.4	The Shower Room shall have two airlocks, one adjacent to the clean room and one adjacent to the equipment room.  The Shower room shall provide hot and cold running water and soap and towels.  It should have adequate space for a shower stall.  Waste water from the shower shall be discharged through a water filtration unit efficient to 5 microns, then to a sanitary sewer. Shower room shall have opaque walls.

3.8.4.1			Shower Stall:  Provide leak tight shower enclosure unit with integrated drain pan fabricated from fiberglass or other durable waterproof material.  Equip with hose bibs for hot and cold water.  Arrange water shut off and drain pump operation controls so that a single individual can shower without assistance from either inside or outside of the abatement work area. Provide splash proof entrances.  Provide back flow prevention device and vacuum breaker, where required.  Connect drain to a reservoir, pump water from reservoir through filters to a drain.  Mount filters inside shower stall in manner that allows for access for filters to be changed from inside the shower. Change filters daily or more often if necessary. Locate filters inside shower unit so that water lost during filter changes is caught by shower pan. Provide temporary extensions of existing (if available and authorized for Contractor use by COTR) hot and cold water and drainage, as necessary for a complete and operable shower.

3.8.4.2			Filtered Waste Water Drainage:  Provide cascaded disposable HEPA filter units on drain lines from showers or any other fluid source carrying ACM.  Connect so that discharged water passes primary filter and output of primary (particles 20 microns and smaller) filter passes through secondary (particles 5 microns and smaller) filter.

3.8.4.3			Sump Pump:  Provide totally submersible waterproof sump pump with integral float switch. Provide unit sized to pump 2 times the flow capacity of all showers or hoses supplying water to the sump, through the filters specified herein when they are loaded to the extent that replacement is required. Provide unit capable of pumping debris, sand, plaster or other materials washed off during decontamination procedures without damage to mechanism of pump.  Adjust float switch so that a minimum of 75 mm remains between top of liquid and top of sump pan.

3.8.5	The Equipment Room shall have two airlocks, one adjacent to the abatement work area and one adjacent to the shower room.  The room shall be of sufficient size so as to accommodate at least one worker to change clothes, and temporarily house any equipment which the contractor wishes to store when not in use.  The area shall have facilities for decontaminating material and equipment, and a container lined with 0.15 mm polyethylene bag for collection of disposable coveralls and foot coverings.

3.8.6	Waste Load-Out Enclosure:  Asbestos-contaminated waste that has been containerized shall be transported out of the abatement work area either through the personnel/equipment decontamination enclosure or through a separate waste load-out enclosure.  If a separate enclosure is used, it shall be built with two airlocks, with curtained doorways: one to the abatement work area and one to an uncontaminated area outside the abatement work area.

3.9	Air Circulation Inside Containment Barrier

3.9.1	Formula for Quantity of Air-Filtration Units: The number of air filtration units needed to achieve the required air circulation rate shall be determined by the following formula:

================================================

CALCULATE			Volume of abatement work area (CF)

MULTIPLY BY		Number of air changes per

hour, four to ten.

MULTIPLY BY	  	1/60 (hr/minutes)

DIVIDE BY 		Capacity of air filtration unit fully loaded with all filters (pressure differential activates warning light for loaded filters)

DIVIDE BY 			80% expected efficiency

ADD					one additional unit as backup

for machine failure or shutdown

EQUALS			minimum number of units

required

================================================

3.9.2	Supplemental Makeup Air Inlets:  As necessary to achieve air flow throughout the abatement work area, locate auxiliary makeup air inlets as far away as possible from the air filtration units, preferably near the ceiling and away from barriers that separate the containment barriers and enclosures from surrounding areas.  Cover inlet with plastic sheeting flaps to reseal automatically if the pressure differential system should shut down for any reason.  Provide rigid framing around the opening.  Spray the flap and around opening with spray adhesive so that if flap closes, the meeting surfaces are both covered with adhesive.  Use adhesive that forms contact bond when dry.  If used during clearance monitoring, tape or seal HEPA filters over inlets.

3.9.3	Penetrations through masonry and/or fire walls, required for improving air circulation, shall be protected with a fire damper.

3.9.4	Accomplish the pressure differential by exhausting a sufficient volume of HEPA filtered air from the abatement work area.  Efforts to achieve pressure isolation shall first address:

3.9.4.1			Establishing required air circulation

3.9.4.2			Verifying seals are complete as practical

3.9.4.3			Establishing increased pressure in adjacent areas, if available

3.9.4.4			Exhausting sufficient volume of HEPA filtered air with additional air filtration units.

3.9.4.5			Decreasing the size of abatement work area to affect a smaller volume required for filtration

3.10	Placement of Air Filtration System Units

3.10.1	Equipment shall be located so as to optimize air movement throughout the abatement work area by positioning air filtration units as far away as practical from the access opening or other supplemental make-up air inlets.

3.10.2	The auxiliary air-filtration unit shall be located on site and available and ready to run at any time.

3.10.3	Air movement shall be established in such a way that air borne fibers will be carried away from workers' breathing zones.

3.10.4	Dead air pockets shall be minimized by proper ducting of make-up air if necessary, and by optimum location of the negative air filtration units.

3.10.5	The Contractor shall use smoke tubes to determine if dead air spots are present, and shall take corrective action as outlined above when they are found. Report such actions to the COTR immediately.

3.10.6	The air filtration units shall be placed so that access for changing the filters is inside the containment barrier.  The unit is to run continuously during filter changing.  A supply of filters shall be kept on site outside of containment area.  If a unit must be turned off for servicing, an auxiliary unit must be in place and turned on.

3.10.7	Vent to the outside of the building, whenever practical, as determined by the COTR.  Units may be vented inside the building only if outside venting is impractical.  Units venting inside a building must be vented through an expansion chamber or diffuser system (self-contained water baffle) to reduce exhaust air velocity.  A secondary HEPA unit may also be used after the expansion chamber/diffuser.  Terminal exhaust ductwork must be placed as far away as possible from occupied areas.  Special provisions for air monitoring shall be implemented by the SI air monitoring firm.

3.10.8	Mount units to exhaust directly or through disposable ductwork.  Use ductwork and fittings of same diameter or larger than discharge connection on fan unit.  Use spiral wire-reinforced flex duct in lengths not greater than 15 meters.  If direction of discharge from fan unit is not aligned with duct use sheet metal elbow to change direction.  Use six feet of spiral wire reinforced flex duct after direction change.

3.10.9	All HEPA units shall be tested in-place before removal begins.  Test will be the responsibility of the contractor.

3.11	Pressure Differential Isolation

3.11.1	The abatement work area and the decontamination enclosure system shall be maintained at a negative pressure relative to adjacent areas.  The relative pressure differential when measured across any physical or critical barrier must continuously equal or exceed a static pressure of 0.5 mm of water. Measurement shall be by manometer or magnahelic gage.

3.11.2	Minimum 4 air changes per hour.  Continuous HEPA filtered exhaust unit is to be in operation until job is completed.

3.11.3	Make-up air shall be obtained only through the decontamination enclosure facilities, or as provided in Section 3.9.2 of these specifications.

3.11.4	Where asbestos-containing material covers an opening or joint, provide negative air pressure sufficient to draw air from the adjoining space into the containment barrier when the opening or joint is exposed after asbestos removal.  Seal newly exposed openings and joints immediately to prevent contamination of adjoining spaces.

3.11.5	Supply sufficient pre-filters to allow frequent changes.

3.11.6	During and after the pre-abatement test, run the air filtration units continuously to maintain a constant pressure differential and air circulation until decontamination, cleaning, and encapsulation of the abatement work area is complete.

3.11.7	The HEPA-filtered units shall be left on continuously until after final clearance air measurement of 0.01 f/cc or the pre-removal background level, whichever is lower is achieved, and the COTR authorizes the shut-down of the units.  Where feasible, the units shall be left on until the enclosure is completely removed.

3.11.8	HEPA units must be set up to cause an alarm-bell or buzzer to sound should the HEPA filter become clogged or the exhaust unit fails in operation after working hours. The alarm must be loud enough to alert a SI Security Officer of the equipment failure. The guard will phone a previously designated contractor employee whose 24-hour number shall have been recorded at the beginning of the project.  The notified contractor will immediately dispatch a repair crew to the job site.  A spare HEPA unit shall always be available to immediately restore negative air pressure.

3.11.9	If the pressure differential between inside and outside the containment barrier drops to 0.4 mm of water, the Contractor will immediately inspect the containment for sources of pressure leaks and report actions taken to the SI IH and COTR.  The system warning alarm shall sound if pressure drops below 0.03 mm of water, and work shall stop.

3.12	Pre-Abatement Inspection, Testing, and Approval

3.12.1	Pre-Abatement Testing Requirements: Contractor must demonstrate with continuous data log that abatement work area can hold negative pressure of 0.5 mm of water for a minimum of 2 hours, prior to commencement of actual asbestos removal, unless the system is exhausted through an isolated ventilation system.  In this case, the test period shall be long enough to ensure that the lock-out ventilation controls are not over ridden and the HVAC system does not reactivate.  As a minimum, the Contractor shall make all arrangements and demonstrate satisfactory equipment operation and set-up for compliance with these specifications.

3.12.1.1		Show proper condition of equipment seals including results of in-place HEPA-filter testing.

3.12.1.2		Show proper operation of safety and warning devices.

3.12.1.3		Show proper operation and calibration of instrumentation.

3.12.1.4		Show identification of equipment unit and fan capacity.

3.12.1.5		Use smoke tubes to demonstrate adequate air circulation, elimination of dead air pockets, and positive air motion through the decontamination enclosure system into the abatement work area.

3.12.1.6		Show the installation method for pre-filters and the HEPA primary filter in the air filtration unit. Show supply of filters available on site.

3.12.1.7		Demonstrate and record that a minimum 0.50 mm of water pressure differential has been achieved and can be maintained.

3.12.1.8		Demonstrate procedures for how workers will enter and exit the decontamination enclosure system.

3.12.1.9		Demonstrate procedures for handling emergencies and for the prevention of contamination of surrounding areas.

3.12.1.10	With COTR and Building Representative, identify disabled building ventilation systems and the positive means that will prevents accidental or premature restarting. Confirms means to have unit restarted at the conclusion of the abatement work. With COTR and Building Representative, verify that all equipment affected is secured at the main breaker.

3.12.1.11		Demonstrate how contaminated shower water is filtered and drained.

3.12.1.12		Use a pressure differential meter or manometer to demonstrate the required pressure differential at every barrier separating the abatement work area from the balance of the building, equipment, ductwork or outside.

3.12.1.13		Demonstrate that each air filtration unit is serviced by a dedicated minimum 115V-20A circuit with GFCI protection.

3.12.1.14		Demonstrate how asbestos will be removed and bagged for transport.  Identify procedures for hauling through the building to the loading dock.

3.13	Maintenance of Containment Barrier and Enclosures

3.13.1	Ensure that the containment barrier, decontamination enclosure rooms, and other sealed doors, vents, etc., and plastic linings are effectively sealed and taped for the duration of the abatement work.

3.13.2	Repair damaged barriers and remedy defects immediately upon discovery.  Visually inspect enclosure at the beginning of each work period.

3.13.3	Damaged or deteriorating materials shall not be used and shall be removed from the premises. Material that becomes exposed to and contaminated with asbestos shall be decontaminated or disposed of in accordance with the applicable regulations and special requirements.

3.13.4	Clean debris and residue from inside of the decontamination enclosure system on a daily basis.  Damp wipe or hose down all surfaces after each shift change. Clean debris from shower pans on a daily basis.

3.13.5	Maintain floors in the clean room and airlocks as dry as possible to minimize slips and trips. Damp wipe all surfaces twice after each shift change with a disinfectant solution.

3.14	Removal of Asbestos-Containing Materials (ACM) - General

3.14.1 Prohibited Work Practices.  The following methods shall not be used for work related to or disturbing asbestos, regardless of exposure level:

3.14.1.1	High-speed abrasive disc saws that are not equipped with point of cut ventilation or enclosures with HEPA-filtered exhaust air.

3.14.1.2	Compressed air used to remove asbestos, or materials containing asbestos, unless the compressed air is used in conjunction with an enclosed ventilation system designed to capture the dust cloud created by the compressed air.

3.14.1.3	Dry sweeping, shoveling or other dry cleanup of  dust and debris containing ACM and PACM.

3.14.1.4	Employee rotation as a means of reducing employee exposure to asbestos.

3.14.2	Methods of Compliance.  The following engineering controls and work practices shall be used, at a minimum, for all asbestos tasks:

3.14.2.1 	HEPA-filtered vacuum cleaners.

3.14.2.2	Wet methods.

3.14.1.3	Prompt cleanup and disposal.

3.14.3	The following work shall be done only after the decontamination facilities have been constructed, the area has been isolated and can be maintained under negative air pressure as specified in the previous section, pre-abatement background sampling has been conducted, and arrangements have been made for disposing waste at an acceptable site.

3.14.4	Start abatement work at a location farthest from the fan units and proceed toward them.  If an electric power failure occurs, immediately stop all abatement work and do not resume until power is restored and negative air filtration units are operating again.  Immediately notify COTR of occurrence.  Any torn or unsealed plastic sheeting shall be immediately repaired.  Floor sheeting shall be replaced if damaged.

3.14.5	Wet Removal:  Prior to stripping and/or tooling, the asbestos material shall be sprayed using an airless pump and wetting agents (amended water or removal encapsulant) to enhance penetration and reduce fiber dispersal into the air.

3.14.5.1		A fine spray of amended water shall be applied to reduce fiber release preceding the removal of the asbestos material.  The material shall be sufficiently saturated to prevent emission of excessive airborne fibers.

3.14.5.2		Spray material repeatedly during the abatement work process to maintain a continuously wet condition.  If a removal encapsulant is used, apply in strict accordance with manufacturer's instructions.  Perforate outer covering of any insulation which has been painted and/or jacketed in order to allow penetration of water, amended water or removal encapsulant.  Where necessary, carefully strip away while simultaneously wetting the insulation to minimize dispersal of asbestos fibers into the air.

3.14.5.3		Remove materials in manageable quantities and control the descent to the staging or floor below.  If over 6 meters, use drop chutes to contain material during descent.

3.14.6	Gross removal of dust and debris from contaminated material, material containers, and equipment shall be accomplished in the containment barrier before removal to the equipment decontamination room for wet sponging before leaving the abatement work site.

3.15	Requirements for Specific ACM and Methods - Fireproofing/Soundproofing on Scratch Coat or Wire Lath

3.15.1	Spray asbestos-containing fireproofing or architectural acoustic finish with a fine mist of amended water.  Allow time for amended water to saturate materials to substrate.

3.15.2	Spray the asbestos-containing material repeatedly during the abatement work to maintain wet condition but do not use excessive amounts of water that results in ponding or entry into other areas of the building.

3.15.3	Do not over-saturate to cause excess dripping.  Scrape materials from substrate.  Remove residue remaining on scratch coat after scraping using stiff nylon bristled hand brush.  Use high pressure washer only with written authorization from the COTR.

3.15.4	Remove the saturated asbestos-containing material in small sections.  Do not allow material to dry out.  As it is removed, place the material in sealable plastic bags of 0.15 mm minimum thickness.

3.15.5	Carefully lower removed  and bagged asbestos-containing  material to the floor without dropping  or throwing, or transport to the floor via dust-tight chutes or containers, in accordance with the procedures set forth in 40 CFR 61.147.

3.15.6	Cut wire lath into 50 mm x 150 mm sections and cut hanger wires.  Roll or fold up complete with asbestos-containing material and hand place in container.  Do not drop on floor.  After removal of lath and asbestos-containing material remove any overspray on decking and structure above using stiff nylon bristled brush.  Use one of the following methods for containing waste.

(a)	Wrap material in felt and place in fiberboard drum lined with two disposal bags. Use caution to insure that all edges of wire lath that could cut plastic are covered with felt.

(b)	Place material directly in a steel drum. Use waste containers which are impervious to puncture, leakage, tearing, or ripping from wire lathe.

3.16	Requirements for Specific ACM and Methods - Vinyl Asbestos Tile (VAT) and Mastic

3.16.1	Full containment barriers, with pressure differential ventilation units, shall be used. Dispose as ACM.

3.16.2	Removal of asbestos-containing floor tile and mastic shall be performed in accordance with the procedure outlined below.

(a)	Prepare abatement work area as previously specified for the abatement work.

(b)	Spray areas of asbestos-containing material with amended water  using spray equipment capable of providing a "mist" application to reduce the release of fibers. Wet the material sufficiently to maintain dust control.  Spray the asbestos-containing material repeatedly during work process to maintain wet condition but do not use excessive amounts of water.

(c)	Do not break the individual tiles to remove them.  Gently pry up a corner of the tile with a broad blade putty knife and slip the knife between the tile and the substrate while cutting the mastic bond.

(d)	If the mastic is especially tenacious, use a heat gun to loosen the bond between the tile and the substrate and to make the tile more pliable.

(e)	Non-toxic organic solvents may be used to remove mastic.

(f)	Continuously use a HEPA vacuum around the individual tiles that are being removed.  Do not allow any dust or debris to accumulate on the floor or other surfaces of the abatement work area.

(g)	Do not allow dislodged tiles to dry out. As it is removed, place the material in sealable plastic bags of 0.15 mm minimum thickness.  Place sealed asbestos debris in second 0.15 mm plastic bag, appropriately labeled, and remove from abatement work area.

(h)	After removal of asbestos-containing material, wet-clean all surfaces in the abatement work area to remove residual accumulated material. Continue wet-cleaning until surfaces are visibly free of material.

*****OR USE THE FOLLOWING STANDARD FOR FLOOR TILE*****

3.16.3	Removal of asbestos-containing floor tile and mastic, baseboard and mastic shall be performed in accordance with the procedure outlined below.

(a)	All critical barriers, including ventilation openings (supply and exhaust), lighting fixtures, clocks, doorways, windows, speakers, and other openings into the work area shall be individually sealed with 0.15 mm plastic sheeting and tape.  Elevator doors, fire extinguisher cabinets and all other penetration in the floor, walls, or ceiling shall be sealed in the abatement work area.

(b)	Prepare a worker and/or equipment decontamination and waste load-out enclosure as previously specified.

(c)	Cover all walls in the abatement work area with two layers of 0.15 mm polyethylene sheeting and seal with duct tape or spray-glue.  The sheeting shall be applied to a height of 1.5 m above the floor.  The seams shall be staggered and separated by at least 150 mm.

(d)	Wet asbestos-containing materials with amended water to minimize fiber release during removal.  Use amended water sparingly to eliminate standing water and to prevent water from traveling on the floor.

(e)	Remove tiles individually and minimize breakage.  Heat guns may be used to heat tile and soften the adhesive.  Immediately place tiles in disposal bags.

(f)	Non-toxic organic solvents may be used to remove mastic.

(g)	Wet clean all surfaces to remove residual material.  Continue cleaning until abatement work area is free of visible material.

(h)	Proceed to clearance testing following approval from COTR that abatement work area is visually free of asbestos-containing materials.

3.17	Requirements for Specific ACM and Methods - Roofing

Use the wet removal method for ACM to eliminate visible emissions in accordance with NESHAP regulations. Controls shall be used to prevent re-entrainment into building HVAC system. Dispose as ACM.

(a)	Spray large areas of asbestos-containing roofing material thoroughly with amended water using spray equipment recommended by surfactant manufacturer capable of providing a "mist" application to reduce the release of fibers. Spray the asbestos material repeatedly during the abatement work process to maintain wet conditions, but do not use excessive amounts of water that result in ponding or entry into building.

(b)	Remove the asbestos-containing material in small sections.  Do not allow material to dry out. As it is removed, place the material in sealable plastic bags of 0.15 mm minimum thickness.  Place sealed asbestos debris in second 0.15 mm plastic bag, appropriately labeled, and remove from abatement work area.

(c)	Carefully lower removed and bagged asbestos-containing material to the ground without dropping or throwing, or transport to the ground via dust-tight chutes or containers, in accordance with the procedures set forth in EPA 40 CFR 61.147 Code of Federal Regulations.

(d)	Clean area of all debris and notify COTR for visual inspection.

3.18	Requirements for Specific ACM and Methods – Exterior and Interior Window Caulk

(a)	Exterior: Work will be done from the exterior of the building.  If lifts are needed, lift platforms should be covered with canvass drop cloths.

(b)	Interior: If lifts are needed, lift platforms should be covered with canvass drop cloths.

(c)	Cover the ground or floor area below the abatement work area with 2 layers of 0.15 mm polyethylene sheeting.

(d)	Wet the asbestos-containing materials with amended water to minimize fiber and dust release during removal.  Use amended water sparingly to eliminate standing water and to prevent water from traveling on the ground sheeting.

(e)	Remove the window caulk in small sections using manual methods, not power tools.  Keep the material wet with amended water and do not allow the material to dry out.  As it is removed, place the material in sealable plastic bags of 0.15 mm minimum thickness, and completely seal the bag.  Place sealed debris bag into a second 0.15 mm plastic bag, and completely seal the bag.

(f)	Carefully lower the sealed material debris bag to the polyethylene sheeting on the ground without dropping or throwing.

(g)	After removal of the sealed material debris bags from the work area, HEPA vaccum and wet-clean all surfaces and equipment  in the abatement work area to remove residual accumulated material.  Continue cleaning until the surfaces are visibly free of material.

(h)	Place dropcloths and  other abatement related disposable materials into  sealable plastic bags of 0.15 mm minimum thickness, and completely seal the bag. Place sealed debris bag into a second 0.15 mm plastic bag, and completely seal the bag.  Remove from the work site and dispose as asbestos waste per these specifications.

(i)	Notify COTR for visual inspection.

3.19	Requirements for Specific ACM and Methods - Gypsum Wallboard Joint Compound

(a)	All critical barriers, including ventilation openings supply and exhaust), lighting fixtures, clocks, doorways, windows, speaker, and other openings into the abatement work area shall be individually sealed with 0.15 mm plastic sheeting and tape.  Elevator doors, fire extinguisher cabinets and all other penetrations in the floor wall, or ceiling shall be sealed in the abatement work area.

(b)	Prepare worker/equipment decontamination and waste load-out enclosure as previously specified.

(c)	Isolate the abatement work area by constructing a temporary double layered 0.15 mm polyethylene/stud wall.

(d)	Cover the floor of the abatement work area with 2 layers of 0.15 mm polyethylene sheeting turned up at walls at least 600 mm.

(e)	Wet the asbestos-containing materials with amended water to minimize fiber and dust release during removal.  Use amended water sparingly to eliminate standing water and to prevent water from traveling on the floor.

(f)	Remove the gypsum wallboard and joint compound in small sections.  Do not allow the material to dry out.  As it is removed, place the material in sealable plastic bags of 0.15 mm minimum thickness.  Place sealed debris in a second 0.15 mm plastic bag, and remove from the work area.

(g)	Carefully lower the material to the floor without dropping or throwing.

(h)	After removal of the material, HEPA vacuum and wet-clean all surfaces in the abatement work area to remove residual accumulated material.  Continue cleaning until the surfaces are visibly free of material.

3.20	Requirements for Specific ACM and Methods - Duct Insulation Mastic

(a)	All critical barriers, including ventilation openings (supply and exhaust), lighting fixtures, clocks, doorways, windows, speaker, and other openings into the abatement work area shall be individually sealed with 0.15 mm plastic sheeting and tape.  Elevator doors, fire extinguisher cabinets and all other penetrations in the floor wall, or ceiling shall be sealed in the abatement work area.

(b)	Prepare worker/equipment decontamination and waste load-out enclosure as previously specified.

(c)	Isolate the abatement work area by constructing a temporary double layered 0.15 mm polyethylene/stud wall.

(d)	Cover the floor of the abatement work area with 2 layers of 0.15 mm polyethylene sheeting turned up at walls at least 600 mm.

(e)	Wet the asbestos-containing materials with amended water to minimize fiber and dust release during removal.  Use amended water sparingly to eliminate standing water and to prevent water from traveling on the floor.

(f)	Removed the duct wrap and insulation and the duct mastic in small sections.  Do not allow the material to dry out.  As it is removed, place the material in sealable plastic bags of 0.15 mm minimum thickness. Place sealed debris in a second 0.15 mm plastic bag, and remove from the work area.

(g)	Carefully lower the material to the floor without dropping or throwing.

(h)	After removal of the material, HEPA vacuum and wet-clean all surfaces in the abatement work area to remove residual accumulated material. Continue cleaning until the surfaces are visibly free of material.

3.21	Requirements for Specific ACM and Methods - Contaminated Soils

Saturate dry soil with amended water or a removal encapsulant for a depth of 75 mm.  Remove the top 25mm of soil.  Start removal at the point of work farthest from the entrance to the soil floor area and proceed toward the entrance.  Do not permit traffic into the fresh soil surface.  After the entire first layer of soil is removed, completely change coveralls and at the entrance to the soil removal area don clean boot covers. Use amended water to keep the surface of the soil continuously wet throughout removal and decontamination.  Remove the second 25 mm of soil in the same manner as the first.  Remove the third 25 mm of soil in the same manner as the previous 50 mm.

3.22	Requirements for Specific ACM and Methods - Contaminated Carpeting

Deface carpeting with a light coat of contrasting spray paint before the abatement work.  Coat lightly enough that wetting will not be retarded.  Prior to cutting, thoroughly wet the asbestos-contaminated carpeting to be removed to reduce fiber dispersal into the air.  Accomplish the wetting by using a fine spray (mist) of amended water or encapsulant. Saturate material completely without causing excess dripping.  Allow time for water or encapsulant to penetrate material thoroughly.  Roll up carpeting and dispose of as ACM.

3.23	Requirements for Specific ACM and Methods -Removal of Asbestos-Containing Transite Panels.

(a)	Develop a daily removal plan indicating the square footage of panel material that will be removed during the abatement working day.

(b)	Establish a regulated area by posting necessary barricades and warning signs to isolate the abatement work area.

(c)	Prior to commencing work, establish a regulated area by covering the surface with plastic sheeting a minimum of 4.5 m from the panels being removed.

(d)	At all times, keep the panels misted with water.

(e)	Remove the panels individually and minimize breakage.

(f)	Gently place the panels in bags or wrap the panels in two layers of 0.15 mm plastic sheeting.

(g)	Collect and dispose of any debris that falls on the plastic sheeting as asbestos-containing material.

(h)	Wet-clean all surfaces of the structure which secured the panels to remove residual ACM.

(i)	Encapsulate the structure surfaces wet-cleaned in (h) above.

(j)	Wet wipe the plastic sheeting prior to disestablishing the regulated area and dispose of the sheeting as contaminated waste.

3.24	Requirements for Specific ACM and Methods - Glove-Bag Removal Method

(a)	Preparation:  Before any work commences, a layer of polyethylene sheeting shall be placed on the floor, as a drop cloth, beneath the glove bag abatement work area.  A temporary enclosure shall be constructed around the general removal area to separate it from occupied areas of the building and to serve as a physical barrier should accidental fiber release occur.  Appropriate warning signs shall be posted outside this barrier in areas of high visibility.  A HEPA filtered air filtration unit shall be on-site to be used to contain an emergency fiber release.

(b)	Remove asbestos-containing material inside a glove bag according to manufacturer's guidelines.  Thoroughly wet material to be removed with amended water or removal encapsulant and allow to soak through to substrate.

(c)	Each glovebag shall be installed so that it completely covers the circumference of pipe or other structure where the work is to be done.

(d)	Glovebags shall be smoke-tested for leaks and any leaks sealed prior to use.

(e)	Glovebags may be used only once and may not be moved.

(f)	Glovebags shall not be used on surfaces whose temperature exceeds 65o C.

(g)	Before beginning the operation, loose and friable material adjacent to the glovebag/box operation shall be wrapped and sealed in two layers of 0.15 mm plastic sheeting or otherwise rendered intact.

(h)	Use two people for glove-bag operation. One shall remove insulation, the other shall operate water sprayer and repair any leaks in bag.

(i)	Using a small HEPA vacuum, create a negative pressure inside the glove-bag before starting any asbestos removal and maintain throughout the use of the bag.

(j)	Gently remove insulation from pipe and place it in bottom of bag.

(k)	After removal of insulation, brush and wet-clean pipe to remove residual material. Continue wet cleaning until surfaces are free of visible material.  Clean area of all debris and notify COTR for visual inspection.

(l)	Spray all tools with water inside bag and place back in  pouch.

(m)	Where system uses attached waste bag, such bag shall be connected to collection bag using hose or other material which shall withstand pressure of ACM waste and water without losing its integrity.

(n)	Sliding valve or other device shall separate waste bag from hose to ensure no exposure when waste bag is disconnected.

(o)	Wet and seal visible ends of remaining pipe insulation.

(p)	Spray the inside of the bag with amended water and remove the watering wand, taping the water sleeve closed.

(q)	Tape the make-up air opening closed.

(r)	Using the HEPA-vacuum, collapse bag and seal off lower portion containing asbestos-containing material and gloves of the bag.

(s)	Remove bag from pipe and tools from pouch.

(t)	Glove-bag shall be considered the first container for material.  Dispose of properly.

(u)	Encapsulate abated section of pipe and any adjacent pipe as required.

(v)	Accidental Fiber Release During Glove Bag Removal:  If the glove bag is accidentally cut open, duct tape from inside the bag shall be used to seal the opening.  If the glove bag should rupture during abatement, the drop cloth sheeting beneath the bag shall be used to contain the bag by bringing the edges together, twisting, taping and folding over in gooseneck fashion and taping again.  The area around and under this cloth shall be cleaned with a HEPA vacuum.

3.25	Requirements for Specific ACM Methods:  Negative Pressure Glove Box Systems

Negative pressure glove box systems shall be used to remove ACM or PACM from pipe runs with the following specifications and work practices:

(a)	Glove boxes shall be constructed with rigid sides and made from metal or other material which can withstand the weight of the ACM and PACM and water used during removal.

(b)	A negative pressure generator shall be used to create negative pressure in system.

(c)	An air filtration unit shall be attached to the box.

(d)	The box shall be fitted with gloved apertures.

(e)	An aperture at the base of the box shall serve as a bagging outlet for waste ACM and water.

(f)	A back-up generator shall be present on site.

(g)	Waste bags shall consist of 0.15 mm thick plastic, double-bagged before they are filled, or plastic thicker than 0.15.mm.

Work Practices:

(a)	At least two persons shall perform the removal.

(b)	The box shall be smoke tested prior to each use.

(c)	Loose or damaged ACM adjacent to the box shall be wrapped and sealed in two layers of 0.15 mm plastic prior to the job, or otherwise made intact prior to the job.

(d)	A HEPA filtration system shall be used to maintain pressure barrier in box.

3.26	Requirement for Specific ACM Methods:  Water Spray Process System

A water spray process system may be used for removal of ACM and PACM from cold line piping if, employees carrying out such process have completed a 40-hour separate training course in its use, in addition to training required for employees performing Class I work.  The system shall meet the following specifications and shall be performed by employees using the following work practices.

Specifications:

(a)	Piping shall be surrounded on three sides by rigid framing.

(b)	A 360 degree water spray, delivered through nozzles supplied by a high pressure separate waterline, shall be formed around the piping.

(c)	The spray shall collide to form a fine aerosol which provides a liquid barrier between workers and the ACM and PACM.

Work Practices:

(a)	The system shall be run for at least ten minutes before removal begins.

(b)	All removal shall take place within the water barrier.

(c)	The system shall be operated by at least three persons, one of whom shall not perform removal, but shall check equipment, and ensure proper operation of the system.

(d)	After removal, the ACM and PACM shall be bagged while still inside the water barrier.

3.27	Requirement for Specific ACM Methods:  Mini Enclosure

A small walk-in enclosure which accommodates no more than two persons may be used if the disturbance or removal can be completely contained by the enclosure with the following specification and work practices.

Specifications:

(a)	The fabricated or job-made enclosure shall be constructed of 0.15 mm plastic or equivalent.

(b)	The enclosure shall be placed under negative pressure by means of a HEPA filtered vacuum or similar ventilation unit.

Work Practices:

(a)	Before use, the mini-enclosure shall be inspected for leaks and smoke tested to detect breaches, and breaches sealed.

(b)	Before reuse, the interior shall be completely washed with amended water and HEPA-vacuumed.

(c)	During use air movement shall be directed away from the employee’s breathing zone within the mini-enclosure.

3.28	Requirements for Specific ACM and Methods - Dry-Removal of Electrical Equipment

Do not begin dry removal work until authorized in writing by the EPA NESHAP coordinator and the COTR. A State regulatory authority waiver may be required and if so shall be obtained by the contractor.  Use where wetting may create a hazard for workers or damage equipment or finishes, such as electrical closets, transformer vaults, high pressure steam lines, etc. Work on active electrical equipment is to be performed by qualified trades person with prior experience in the installation or repair of the involved equipment. Restrict access to electrical equipment.

3.29	Post Removal:  Cleaning and Clearance

3.29.1	Provide general clean-up of abatement work area concurrent with the removal of all asbestos-containing materials.  Do not permit accumulation of debris on workspace floor.

3.29.2	Do not perform dry dusting or dry sweeping.

3.29.3	Maintain the minimum required pressure differential of 0.50 mm of water inside the abatement work area enclosure at all times, and until the COTR authorizes the Contractor to remove the enclosure.

3.29.4	During decontamination of automatic sprinkler and smoke detectors, the Smithsonian security office must be contacted for possible nuisance alarms.  Care must be taken in the wiping down of the sprinkler heads and smoke detectors so as not to damage them.  Smoke detectors must be vacuumed clean as directed by the Fire Alarm Shop, Office of Physical Plant.

3.29.5	Initial Phase Cleanup Sequence

(a)	Remove all visible accumulations of asbestos-containing  material and debris.

(b)	Wet clean and HEPA-vacuum all surfaces in the abatement work area.

(c)	Clean all equipment (excluding that which will be needed for further cleaning phases) used in the abatement work area and remove from abatement work area via the Equipment Decontamination Enclosure.

(d)	Remove the top layer (secondary barrier) of plastic sheeting, change all air filtration system pre-filters, and proceed with the second cleaning.

(e)	Replace all HEPA-filters and pre-filters in air filtration air machines with clean filters. Clean all air filtration machines.

(f)	Notify SI IH for observation of cleaning to determine completeness.  Plastic sheeting surfaces will be considered clean when free from dust, dirt, residue, film, or discoloration resultant from abatement operations or other activities subordinate to these operations.

(g)	Perform no activity in abatement work area for at least 12 hours in order to allow settlement of airborne fibers.  No reduction in this settling period will be allowed.

3.29.6	Secondary Phase Cleanup Sequence

(a)	Wet clean and HEPA-vacuum all surfaces in abatement work area at least one more time.

(b)	Notify SI IH for observation to determine completeness of cleaning.

(c)	SI IH will perform a visual observation of the abatement work area in general accordance with ASTM 1368, Standard Practice for Visual Inspection of Asbestos Abatement Projects.

(d)	If visual clearance is not attained, then subsequent re-cleaning will be required.  This sequence will continue until visual clearance is attained.

(e)	When visual clearance has been obtained, the plastic barriers down to the critical barriers may be removed.

3.29.7	Final Air Clearance Testing.

(a)	SI IH will test for the final air clearance levels, in accordance with 3.5.7 of this specification, when areas have passed the visual clearance phase. Final air testing shall be performed using aggressive air sampling techniques.

(b)	Re-clean and continue to clean at Contractor's expense, areas which do not comply with the specified final clearance level.

3.29.8	Consider abatement work areas and all other decontaminated and cleaned areas clean when:

(a)	All phases of clean up have been completed and level of cleanliness is approved by COTR.

(b)	All asbestos final clearance testing results will be as specified in 3.5.7 of this specification.

3.29.9.	After area passes final air clearance dismantle Decontamination Enclosure Systems and thoroughly HEPA-vacuum and wet clean immediate areas.

3.29.10 Dispose of debris from removal operation, used cleaning materials, unsalvageable materials used for sturdy barriers, and any other remaining materials.  Consider the materials to be contaminated, and dispose of accordingly.

3.29.11 The "COTR's Certification of Visual Inspection and Final Air Sampling for Asbestos Abatement" form  (see page 45) or equivalent shall be completed, signed by the Contractor, SI IH, COTR and included with the  COTR project records.  The COTR shall provide written results of all visual inspections and final clearance testing to the facility safety coordinator.

3.30	Post Clearance:  Application of Lockdown Encapsulant To Base Material

3.30.1	Pre-Lockdown Encapsulant Mock-up Test:  Prior to beginning lockdown encapsulant work, provide a sample area for approval by the COTR.  Notify the COTR a minimum of 72 hours in advance to schedule the test.  Lockdown encapsulant shall be applied using methods set forth in ASTM Proposed Specification P-189 "Specification for Encapsulants for Friable Asbestos Containing Building Materials".  The test must be witnessed by the COTR or as otherwise designated by the COTR.  The approved procedures and materials shall serve as a standard for the balance of the lockdown encapsulant work.

3.30.2	Apply encapsulant only when environmental conditions in the abatement work area are as required by the manufacturer's instructions and the COTR.  Prior to applying any encapsulant, ensure that its application will not cause the base material to fail and allow the encapsulated material to fall of its own weight or separate from the substrate.

3.30.3	Apply encapsulant with an airless spray gun with air pressure and nozzle orifice or as otherwise recommended by the encapsulant manufacturer.

3.30.4	Encapsulant Application to Plaster Scratch Coat:  Apply two coats of encapsulant to the scratch coat plaster after all ACM has been removed.  Apply in strict accordance with the manufacturer's printed instructions.  Any deviations from such printed instructions must be approved by the COTR in writing prior to commencing work.

3.30.4.1		Apply the first coat of encapsulant while the plaster scratch coat is still damp from the asbestos removal procedures.  If the surface has been permitted to dry, vacuum surface with a HEPA vacuum prior to applying the encapsulant.

3.30.4.2		Apply second coat over first coat in strict conformance with manufacturer's instructions.

3.30.4.3		Color the encapsulant with contrasting colors in alternate coats so that visual confirmation of complete and uniform coverage of each coat is possible.  Adhere to manufacturer's instructions for coloring.  At the completion of work, the encapsulated surface must be a uniform third color produced by the mixture.

3.30.4.4		Sealing Exposed ACM edges:  Prior to encapsulation, permit the exposed edges to dry completely to permit penetration of the encapsulant.  Seal edges of ACM with two coats of encapsulant.  Label the joint for the portions which are asbestos and non-asbestos.

3.31	Containment Barrier Removal

3.31.1	Following area final clearance and lockdown encapsulation, leave pressure differential units running as long as feasible during containment barrier removal.

3.31.2	Equipment, machinery, scaffolding, tools, etc., within the abatement work area shall not be removed without first being thoroughly cleaned with amended water or in the case of delicate items susceptible to rust, an acceptable substitute.

3.31.3	After the abatement work area is found to be in compliance, the remaining sealed areas and exits are unsealed and the plastic sheeting, tape, and any other trash and debris are disposed of in sealable plastic bags and treated as asbestos waste. The SI IH will conduct a final walkthrough and document results for the COTR.

3.31.4	Before removal from the abatement work area, remove and properly dispose of pre-filter, decontaminate exterior of machine and seal intake to the machine with 0.15 mm polyethylene to prevent environmental contamination from the filters.

3.31.5	The contractor shall patch and paint and repair all damaged areas and restore them to their original, pre-contract condition.

3.32	Waste Disposal

3.32.1	The COTR reserves the right to restrict when containerized ACM will be moved outside of the abatement work area and pass through the building. Times chosen to move containerized ACM in the building shall be during non-public hours and when limited staff is in attendance or under other appropriate conditions as determined by the COTR.

3.32.2	Asbestos-contaminated waste that has been containerized shall be transported out of the abatement work area either through the personnel/equipment decontamination enclosure or through a separate waste load-out enclosure.  Waste load-out procedures shall be performed by two teams.  The team inside the abatement work area shall clean the outside of properly labeled asbestos waste containers using HEPA vacuums and/or wet wiping, and place them into the waste load-out enclosure.  No personnel from the inside team shall exit any further from the abatement work area.  The team inside the waste load-out area (wearing protective clothing and respirators) shall retrieve the waste containers from the load-out enclosure, double-bag the waste and pass them to an uncontaminated area outside the enclosure.  No unprotected personnel from the outside team shall enter this enclosure.  As applicable, routes to the elevator, the elevator itself, and route to covered carts shall be lined with polyethylene sheeting.

3.32.3	For Amosite Fibers:  If the material contains amosite fibers, evacuate air from disposal bags with a HEPA vacuum before sealing.

3.32.4	Water not disposed of with the asbestos-containing materials shall be filtered to remove asbestos fibers and debris before disposal into sanitary sewer.

3.32.5	Do not store containerized materials outside of the abatement work area. Take containers from the abatement work area directly to a sealed truck or dumpster.

3.32.6	Bulk and containerized asbestos waste shall be packed, labeled, and transported according to DOT Regulations 49 CFR 173.216 and 49 CFR 173.240.  All removed ACM, plastic sheeting, tape, cleaning material, clothing, and all other disposable material or items used in the abatement work area shall be packed into double bagged sealable 0.15 mm plastic bags or double containerized with one bag and one drum.  The bags shall be marked with the labels required by OSHA 29 CFR 1910.1001 and/or 1910.1200, and 1926.1101.

3.32.6.1		If the asbestos waste can reasonably be expected to damage double bagged 0.15 mm plastic bags, the following barrel decontamination procedures shall be followed.

(a)		Line barrels with a 0.15 mm plastic liner to prevent leaking of contaminated material from the containers.

(b)		As bags are moved out through the decontamination system, wet wipe bags to remove all contamination from them before they are moved into an uncontaminated space.

(c)		Place bagged waste into appropriately labeled barrels for transport to landfill.

(d)		After bagged contaminated waste is placed in barrels, seal lids on barrels.

3.32.6.2		Minimum labeling required:

First Label:

================================

DANGER

CONTAINS ASBESTOS FIBERS

AVOID CREATING DUST

CANCER AND LUNG DISEASE HAZARD

================================

Second Label:

=================================================

PROVIDE IN ACCORDANCE WITH U.S. DEPARTMENT OF TRANSPORTATION REGULATION ON HAZARDOUS WASTE MARKING.  49 CFR PART 172, SUBPART D: "RQ ASBESTOS NA 2212". PROVIDE A "CLASS 9" LABEL, PER 49 CFR PART 172, SUBPART E.

=================================================

3.32.6.3		Notify COTR prior to removing each trailer or other waste transport from the jobsite.

3.32.6.4		Notify COTR not less than 48 hours prior to the proposed time of delivery of contaminated waste to the landfill.  Owner may elect to observe this operation.

3.32.6.5		The Contractor shall transport the approved sealed drums to an approved waste disposal site.

3.32.6.6		Allow only sealed plastic bags or impermeable containers to be deposited in landfill. Leave damaged, broken, or leaking plastic bags in the impermeable container and deposit entire barrel in landfill.

3.32.6.7		Ensure that there are no visible emissions to the outside air from site where materials and waste are deposited.

3.32.7	Contractor shall submit a disposal certificate from the EPA approved landfill confirming final disposal in accordance with EPA standards and regulations before final payment. Retain receipts from landfill or processor for materials disposed off. At completion of hauling and disposal of each load, submit copy of waste manifest, chain of custody form, and landfill receipt to the COTR.

3.32.8	The COTR shall provide copies of all hazardous waste disposal manifests to the facility hazardous waste coordinator.

3.33	Job Close-Out

3.33.1	The Contractor shall submit to the COTR, Post Abatement Drawings to indicate location of the asbestos material removed.  If required, the Contractor may edit the Project Drawing to show the actual or additional abatement work completed.

3.33.2	The Contractor shall remove from the site all other debris and rubbish resulting from removal and disposal operations and the temporary construction of containment barriers and enclosures.

3.33.3	The Contractor shall use positive means to demonstrate to the COTR that any building utilities that were temporarily disabled are now in full service. Notify the COTR when disabled building ventilation, systems, electrical power, smoke detectors, building access/egress passages may safely be re-started or used.

** END OF SECTION 028200 **

CERTIFICATION OF VISUAL INSPECTION AND FINAL AIR SAMPLING FOR ASBESTOS ABATEMENT

The COTR, Contractor, and SI Industrial Hygienist hereby certify that the abatement work areas have been visually inspected (all surfaces including pipes, beams, ledges, walls, ceiling and floor, plastic sheeting, etc.) and there is no dust, debris, or residue.  The COTR also certifies that final air sample results meet abatement work area clearance specifications.

OEDC Project No	SI Contract No.

Project Title/Location

Date of Inspection

Date and results of final air sample

ASBESTOS		Firm

ABATEMENT 	Print Name

CONTRACTOR	Print Title

Signature

SI		Firm

INDUSTRIAL 	Print Name

HYGIENIST		Print Title

Signature

SI		Firm

COTR		Print Name

Print Title

Signature