WATER STORAGE STEEL TANKS – SECTION 331615

TABLE OF CONTENTS

WATER STORAGE STEEL TANKS -  SECTION 331615	1

PART 1 - GENERAL	1

1.01	RELATED DOCUMENTS	1

1.02	SUMMARY	1

1.03	ALLOWANCES	1

1.04	UNIT PRICES	1

1.05	DEFINITIONS	1

1.06	SYSTEM DESCRIPTION	1

1.07	PERFORMANCE REQUIREMENTS	2

1.08	SUBMITTALS	3

1.09	QUALITY ASSURANCE	4

1.10	DELIVERY, STORAGE, AND HANDLING	6

1.11	PROJECT CONDITIONS	6

1.12	COORDINATION	6

1.13	WARRANTY	6

1.14	SERVICE AGREEMENT	7

1.15	EXTRA MATERIALS	7

PART 2 - PRODUCTS	7

2.01	MATERIALS	7

2.02	PIPE	7

2.03	VALVES	8

2.04	PRESSURE GAUGE	8

2.05	ASSEMBLIES	9

2.06	CONCRETE WORK	10

2.07	CHLORINE	11

PART 3 - EXECUTION	11

3.01	FOUNDATIONS	11

3.02	EXCAVATING, FILLING, AND GRADING	11

3.03	CATHODIC PROTECTION	11

3.04	OBSTRUCTION LIGHTING	11

3.05	BEACON	11

3.06	TANK INSTALLATION	11

3.07	INSPECTIONS AND TESTING	11

3.08	PIPING INSTALLATION (EXCEPT FOR OVERFLOW PIPING)	12

3.09	PAINTING AND COATING OF TANK	12

3.10	DISINFECTION	13

3.11	INSPECTION AND REPAIR	13

EDITING NOTE

All bracketed blanks, words, phrases, sentences, and paragraphs in this specification require the editor to either include or delete the bracketed section, or provide required information.

- WATER STORAGE STEEL TANKS -  SECTION 331615

- GENERAL

      - RELATED DOCUMENTS

        - Drawings and General Provision of Contract, including General and Special Conditions and Division 1 Specification Section, apply to work of this Section.

      - SUMMARY

        - Provide all engineering, design, erection, and testing for new elevated storage tank for fire protection service.

      - ALLOWANCES

- [List Allowances, if included as part of the contract. Confirm with OSHEM and COTR]

      - UNIT PRICES

- [List Unit Prices, if included as part of the contract. Confirm with OSHEM and COTR]

      - DEFINITIONS

        - COTR: Contracting Officer Technical Representative

        - FM: FM Global (Factory Mutual)

        - FPE: Fire Protection Engineer

        - Furnish: To supply the stated equipment or materials

        - Install: To set in position and connect or adjust for use

        - NFPA: National Fire Protection Association

        - NICET: National Institute for Certification in Engineering Technologies

        - OSHEM: Office of Safety Health and Environmental Management

        - Provide: To furnish and install the stated equipment or materials

        - UL: Underwriters Laboratories

      - SYSTEM DESCRIPTION

        - New ______gallon (____liter) dedicated fire protection water storage tank. Tank shall be [fluted column] [pede sphere] [standpipe] design.

      - PERFORMANCE REQUIREMENTS

        - Design and Construction Standards

          - National Fire Protection Association (NFPA) 22, Standard for Water Tanks for Private Fire Protection

          - The design, fabrication, and erection of the [elevated tank] [standpipe][reservoir] shall be in accordance with the applicable requirements of AWWA D100 or AWWA D103 except as modified herein. Earthquake design shall be [in accordance with UFC 3-310-04 SEISMIC DESIGN FOR BUILDINGS and Sections 13 48 00 SEISMIC PROTECTION FOR MISCELLANEOUS EQUIPMENT and13 48 00.00 10 SEISMIC PROTECTION FOR MECHANICAL EQUIPMENT] [as indicated]. No additional thickness for corrosion allowance will be required.

          - Design metal temperature shall be [_____] degrees F. The elevated tank shall be designed for a basic wind speed of [_____]mph in accordance with ASCE 7 or designed in accordance with AWWA D100 wind load design, whichever provides the greater pressure. [The elevated tank shall be designed for a snow load of 25 psf [_____]]. The [standpipe][reservoir] shall be designed for a peak wind speed of [_____] and snow load of [_____].

        - Welding

          - Qualification of welding procedures, welders, and welding operators shall be in accordance with Section 8.2 of AWWA D100.

        - Design Requirements

          - The elevated tank shall have a storage capacity of [_____] gallons. The high-water level of tank shall be at elevation [_____] with the top of column foundations at elevation [_____]. The range between high and low water levels shall be approximately [_____] feet. The existing grade at the tank site is approximately elevation [_____]. The top of straight side sheets, where a cone-shaped roof is furnished, shall not be less than 6 inches above the top of the overflow weir. The tank diameter shall be not less than [_____] feet and the riser diameter not less than [_____] feet.

          - The tank shall [be of the style shown] [have an ellipsoidal bottom, with vertical side sheets and a cone shaped top, or shall be of an elliptical or oval design as approved. In the latter design, the lower section of the roof may be used for water storage].

          - The tower supporting the tank shall be constructed of structural shapes of the open type, or of tubular sections, to permit inspection and painting. The tower shall be thoroughly braced with horizontal struts and diagonal ties. The tower columns may be vertical or inclined as the design may require. Main column splices shall be as few as possible and shall be located as near as practicable to the intersection of the centerline of the struts. Splice plates shall be welded so as to hold the members in line and transmit any tension ors hearing stresses to which the members may be subjected.

          - The connections of the tank, with the columns shall be made to distribute the load properly over the column sections and over the shell of the tank.

          - Around the bottom of the tank a balcony meeting the requirements of Section 4.7.2 of AWWA D100 and conforming to all federal or local laws or regulations shall be provided. Balcony floor plates shall be at least 1/4 inch thick and shall be suitably punched or drilled for drainage.

        - Sizing and Design

          - Sizing and design of elevated tank shall be in accordance with Section 4 of AWWA D100. Submit a certificate signed by a registered professional engineer providing: (1) description of the entire tank and foundation structural design loading conditions, (2) description of structural design methods and codes used in establishing allowable stresses and safety factors, (3) statement that the structural design has been checked by experienced engineers specializing in hydraulic structures to ensure that design calculations for member sizes, dimensions, and fabrication processes are as prescribed by ACI and AWWA standards, and (4) certification that the completed work was inspected in accordance with AWWA D100 or AWWA D103 as applicable.

        - [Standpipe] [Reservoir]

          - The [standpipe] [reservoir] shall have a storage capacity of [_____] gallons. The high-water level of [standpipe] [reservoir] shall be at elevation[_____] with the top of foundation approximately at elevation [_____]. The range between high and low water levels will be approximately [_____] feet.

          - Existing grade at proposed location is approximately elevation [_____].The [standpipe] [reservoir] shall have such standard shell height and such diameter as will meet the requirements for the selected standard capacity and for the high-water level specified above.

          - The [standpipe] [reservoir] may have [supported cone roof,] [supported toriconical roof,][self-supporting umbrella roof,] [self-supporting dome roof, or][ellipsoidal roof,] [aluminum self-supporting dome roof,] as approved. The [standpipe] [reservoir] shall be of welded or bolted construction.

        - Coatings Certification

          - Coating materials for interior applications and all other materials which will be in normal contact with potable water shall conform to NSF 61. Certification by an independent third-party organization that all interior coatings and materials, that come in contact with potable water, comply with NSF 61 shall be provided.

      - SUBMITTALS

        - The following shall be submitted in accordance with Section 01 33 00

        - Shop Drawings

          - Tank Installation: Detail and erection drawings, before proceeding with any fabrication. Complete drawings with details of steel, pipe, and concrete work, and of the assembling of items required for the total installation. Use standard welding symbols as recommended by the American Welding Society. Details of welded joints referenced on the drawings shall be included.

        - Product Data

          - System Description

          - Foundations

          - Design Analysis and Calculations

        - Test Reports

          - Tank Installation

          - Testing of Valves and Piping

          - Each coating manufacturer's technical data, application instructions, Material Safety Data Sheets (MSDS), and certificate for compliance for VOC content.

          - Copies of the following test results:

            - Manufacturer's mill test reports for plate material.

            - Mill and shop inspections by a commercial inspection agency.

            - After acceptance of the structure, the radiographic film and test segments.

            - At the conclusion of the work, a written report prepared by the Contractor covering the hydrostatic test and certifying that the work was inspected in accordance with Section 11.2.1 of AWWA D100.

          - Certificates

            - System Description

            - Foundations

            - Certification by an independent third-party organization that all interior coating and materials that come in contact with the potable water comply with NSF 61.

            - A certificate signed by a registered professional engineer, providing the following information:

              - Description of the structural design loading conditions used for the design of entire tank including the foundation.

              - Description of the structural design method and codes used in establishing the allowable stresses and safety factors applied in the design.

              - A statement verifying that the structural design has been checked by experienced engineers specializing in hydraulic structures.

              - A statement verifying that the detail drawings have been checked by experienced engineers specializing in hydraulic structures to determine that they agree with the design  calculations in member sizes, dimensions, and fabricating process as prescribed by applicable ACI and AWWA standards.

      - QUALITY ASSURANCE

        - Manufacturers Qualifications: The publications listed below form a part of this specification to the extent referenced. The publications are referred to within the text by the basic designation only.

          - AMERICAN SOCIETY OF CIVIL ENGINEERS (ASCE)

            - ASCE 7 (2005; Supp 1) Minimum Design Loads for Buildings and Other Structures

          - AMERICAN WATER WORKS ASSOCIATION (AWWA)

            - AWWA B300 (2004) Hypochlorites

            - AWWA B301 (2004) Liquid Chlorine

            - AWWA C104/A21.4 (2003) Cement-Mortar Lining for Ductile-Iron Pipe and Fittings for Water

            - AWWA C105/A21.5 (2005) Polyethylene Encasement for Ductile-Iron Pipe Systems

            - AWWA C110/A21.10 (2008) Ductile-Iron and Gray-Iron Fittings for Water

            - AWWA C111/A21.11 (2000) Rubber-Gasket Joints for Ductile-Iron Pressure Pipe and Fittings

            - AWWA C115/A21.15 (2005) Flanged Ductile-Iron Pipe With Ductile-Iron or Gray-Iron Threaded Flanges

            - AWWA C150/A21.50 (2002; Errata 2003) Thickness Design of Ductile-Iron Pipe

            - AWWA C151/A21.51 (2002; Errata 2002) Ductile-Iron Pipe, Centrifugally Cast, for Water

            - AWWA C500 (2002; R 2003) Metal-Seated Gate Valves for Water Supply Service

            - AWWA C504 (2006) Standard for Rubber-Seated Butterfly Valves

            - AWWA C508 (2001) Swing-Check Valves for Waterworks Service, 2 In. (50 mm) Through 24 In. (600mm) NPS

            - AWWA C600 (2005) Installation of Ductile-Iron Water Mains and Their Appurtenances

            - AWWA C652 (2002) Disinfection of Water-Storage Facilities

            - AWWA D100 (2005; Errata 2007) Welded Steel Tanks for Water Storage

            - AWWA D103 (1997) Factory-Coated Bolted Steel Tanks for Water Storage

            - ASME B16.3 (2006) Malleable Iron Threaded Fittings, Classes 150 and 300

            - ASME B40.100 (2005) Pressure Gauges and Gauge Attachments

          - ASTM INTERNATIONAL (ASTM)

            - ASTM A 197/A 197M (2000; R 2006) Standard Specification for Cupola Malleable Iron

            - ASTM A 48/A 48M (2003) Standard Specification for Gray Iron Castings

            - ASTM A 53/A 53M (2007) Standard Specification for Pipe, Steel, Black and Hot-Dipped, Zinc-Coated, Welded and Seamless

          - MANUFACTURERS STANDARDIZATION SOCIETY OF THE VALVE AND FITTINGS INDUSTRY (MSS)

            - MSS SP-80 (2003) Bronze Gate, Globe, Angle and Check Valves

          - NATIONAL FIRE PROTECTION ASSOCIATION (NFPA)

            - NFPA 24, Standard for Water Tanks for Private Fire Protection.

          - NSF INTERNATIONAL (NSF) NSF 61 (2007a; Addendum 2007) Drinking Water System Components - Health Effects

          - THE SOCIETY FOR PROTECTIVE COATINGS (SSPC)

            - SSPC PS 4.04 (1982; E 2004) Four-Coat White or Colored Vinyl Painting System (For Fresh Water, Chemical, and Corrosive Atmospheres)

            - SSPC PS Guide 17.00 (1982; E 2004) Guide for Selecting Urethane Painting Systems

            - SSPC Paint 104 SSPC Paint 21(1982; E 2004) Paint Specification No. 104White or Tinted Alkyd Paint (1982; E 2004) Paint Specification No. 21White or Colored Silicone Alkyd Paint (Type I, High Gloss and Type II, Medium Gloss)

            - SSPC Paint 25	(1997; E 2004) Paint Specification No.25Zinc Oxide, Alkyd, Linseed Oil Primer for Use Over Hand Cleaned Steel Type I and Type II

      - DELIVERY, STORAGE, AND HANDLING

        - Deliver paint in unopened containers with unbroken seals and labels showing designated name, specification number, color, directions for use, manufacturer, and date of manufacture, legible and intact at time of use.

        - Handle and store water storage tank systems, components, and parts to prevent distortions and other damage that could affect their structural, mechanical, or electrical integrity.

        - Replace damaged items that cannot be restored to original condition.

        - Store items subject to deterioration by exposure to elements, in a well-drained location, protected from weather, and accessible for inspection and handling.

      - PROJECT CONDITIONS

- [List any special project conditions and/or environmental limitations on system installation, such as temperature, humidity, ventilation, etc.

      - COORDINATION

        - Coordinate major equipments and piping layouts with other trades to avoid obstructions and excessive changes in direction for piping.

      - WARRANTY

        - The Contractor shall guarantee labor, materials, and equipment provided under this contract against defects for a period of one year after the date of final acceptance of this work by the Government.

        - Final acceptance includes, but is not limited to, the receipt and OSHEM approval of, as-built drawings and operation and maintenance manuals.

      - SERVICE AGREEMENT

- [List requirements, if part of the contract. Confirm with OSHEM and COTR].

      - EXTRA MATERIALS

- [List special requirements for spare parts, if part of the contract. Confirm with OSHEM and COTR].

- PRODUCTS

      - MATERIALS

        - Provide materials conforming to the following requirements:

          - Steel

          - Shop Fabrication

            - Section 2 of AWWA D100 or Section 2 of AWWA D103.

            - Section 9 of AWWA D100 or Section 7 of AWWA D103.

      - PIPE

        - Ductile-Iron Pipe

          - Pipe for fluid conductors, except for overflow pipe, shall be ductile-iron pipe and shall be either of the following:

        - Bell-and-Plain End Pipe

          - AWWA C150/A21.50 and AWWA C151/A21.51, for not less than 150 psi working  pressure, unless otherwise shown or specified. Joints shall be push-on or mechanical-joint conforming to AWWA C111/A21.11. Pipe shall be cement mortar lined in accordance with AWWA C104/A21.4. Linings shall be standard thickness.

        - Flanged Pipe

          - Flanged pipes shall conform to the applicable portions of AWWA C110/A21.10,AWWA C115/A21.15 and AWWA C151/A21.51, for not less than 150 psi working pressure, unless otherwise shown or specified. Pipe shall have flanged ends in accordance with AWWA C115/A21.15. Pipe shall be cement mortar lined in accordance with AWWA C104/A21.4. Linings shall be standard thickness.

        - Specials and Fittings (except for overflow pipe)

          - Ductile-Iron with Bell-and-Plain End

            - AWWA C110/A21.10 and AWWA C151/A21.51 for not less than 150 psi working pressure, unless otherwise shown or specified. Specials and fittings shall be cement mortar lined in accordance with AWWA C104/A21.4. Linings shall be standard thickness.

          - Ductile-Iron with Flanged Ends

            - AWWA C110/A21.10 and AWWA C151/A21.51 for not less than 150 psi working pressure unless otherwise shown or specified. Fittings shall have flanged ends in accordance with AWWA C110/A21.10. Specials and fittings shall be cement mortar lined in accordance with AWWA C104/A21.4. Linings shall be standard thickness.

        - Fittings for Screw-Joint Pipe

          - Malleable-iron, galvanized, 150 psi, ASTM A 197/A 197M, threaded ends,
ASME B16.3.

        - Joints Inside Valve Chamber

          - All joints inside the valve chamber shall be flanged.

      - VALVES

        - Gate Valves

          - All valves serving water supply and discharge pipes for water storage tanks shall be gate valves or Post Indicator Valves.  Gate valves shall be opened by turning counterclockwise. Valves 3 inches and larger shall be iron body, brass mounted, conforming to AWWA C500. Valves smaller than 3 inches shall be all bronze and shall conform to MSS SP-80, Type 1, class 150. Valves 3 inches or larger located in valve chambers shall be equipped with hand-operating wheels and shall be flanged.

        - Check Valves

          - Check valves shall be of the horizontal swing-check type, suitable for the purpose and the operating conditions. The body shall be iron and shall have a removable gate assembly and a cover removable for inspection. The gate, gate seat, shaft, gate studs, and nuts shall be bronze or other suitable alloy. Valves shall conform to AWWA C508.

        - Altitude Valve

          - The supply to the [elevated tank] [standpipe] [reservoir] shall be controlled by a [_____] inch altitude valve, automatic in operation and accurately set to prevent overflow of the [elevated tank] [standpipe][reservoir]. The valve shall have flanged ends and a heavy cast iron body, shall be bronze fitted with renewable cups and seats, and shall be designed without metal-to-metal seats. The valve shall be cushioned when opening and closing to prevent water hammer or shock. Valves shall be provided with a travel indicator.

      - PRESSURE GAUGE

          - Pressure gauge of the direct-reading type, equipped with a shutoff cock, shall be provided, in the valve chamber, on the tank side and on the discharge side of the check or altitude valve. Gauges shall have 6 inch dials, shall be stem mounted, and shall conform to ASME B40.100. Accuracy of gauges shall be Grade A or better. Gauges shall be calibrated in psi in not more than 2 psi increments from 0 to 50 psi in excess of the normal operating pressure at the tank.

      - ASSEMBLIES

        - Tank Accessories

          - Section 7 of AWWA D100 or Section 5 of AWWA D103 and as specified.
Additional requirements for accessories are as follows:

        - Manholes and Pipe Connections

          - Section 7 of AWWA D100 and Section 5 of AWWA D103 represent the minimum requirements. Number, type, location, and size of manholes and pipe connections shall be as shown on the drawings. Inlet pipe connections to extend [_____] inches above tank bottom and shall be provided with deflectors as shown on the drawings. Outlet pipe connections to extend [_____] inches above tank bottom and shall be provided with vortex breakers as shown on the drawings.

        - Overflow

          - The overflow for the tank shall consist of an overflow weir and [stub overflow] [outside drop pipe, adequately supported and] capable of discharging at a rate of [_____] gpm with [_____] inches of head [, without the water level exceeding [_____]]. [The top of the weir shall be [_____] inches below [_____].] [The weir shall be located as indicated.] The [stub overflow shall be steel, ASTM A 53/A 53M or equal, and shall befitted with a screen] [overflow pipe shall be steel, ASTM A 53/A 53M or equal, and shall terminate 1 to 2 feet above grade and shall be fitted with a flapper valve or screen to prevent ingress of animals and insects].

        - Vent

          - Vent shall be welded to the cover plate of the center manhole on the roof. Vent will be tank manufacturer's standard type mushroom vent with aluminum bird screen. The free area of the vent shall be sized 50 percent in excess of the [_____] gpm pump-in rate and [_____] gpm pump-out rate. Screening for vent shall conform to Section 5.7.2 of AWWA D100 or Section 5.7.2 of AWWA D103which ensures fail-safe operation in the event that screen frosts over and the bottom of the screen shall be sufficiently elevated for snow consideration in the area.

        - Ladders and Safety Devices

          - Ladders and safety devices shall be provided in accordance with Sections7.4 and 7.5 of AWWA D100 or Sections 5.4 and 5.5 of AWWA D103. Location of ladders shall be as shown on the drawings. Sections 7.4 and 7.5 of AWWA D100 and Sections 5.4 and 5.5 of AWWA D103 represent the minimum requirement. In addition, safety cage, rest platforms, roof ladder handrails, and other safety devices shall be provided as required by federal or local laws or regulations.

        - Scaffold Cable Support

          - Provision shall be made for the attachment of a scaffold cable support at the top of the roof on welded tanks.

        - Balconies

          - Provide a balcony a minimum of 2 feet wide with a standard guard railing.  Provide a structural steel railing with a top rail 42 inches above balcony platform with an intermediate rail halfway between. Guard rail shall be capable of withstanding a force of 200 pounds applied in any direction.  Install a steel toe board with minimum height of 4 inches. Bottom of toe board shall be a maximum 1/4 inch from platform top. Extend guard rail and toe board entire length of balcony except where access openings are required. For balcony floors use diamond plates a minimum of 1/4 inch thick, punched or drilled for drainage. [Equip access openings in guardrail with a gate which closes automatically.] Hatches through balcony floor shall be counterbalanced or otherwise arranged to open from below.

        - Coating for Welded Tanks

          - Provide exterior coating systems conforming to Section 09 97 13.27,"Exterior Coating of Steel Structures," and interior coating systems conforming to Section 09 97 13.16, "Interior Coating of Welded Steel Water Tanks."

        - Coating for Bolted Tanks

          - As supplied by the manufacturer.

        - Valve Chamber

          - Valve chamber shall be sufficiently large to house all control valves and fittings. Pipes, valves, and fittings shall be supported on concrete blocks where necessary. The valve chamber shall be constructed to provide not less than [_____] feet of cover over the pipes. The valves and fittings shall extend from the [standpipe] [reservoir] [riser pipe]connection to a point one length of pipe outside the valve chamber walls on the main or feed line to the [elevated tank] [standpipe] [reservoir]; the drain line will be carried to an outlet as indicated on the drawings. The access manhole shall be not less than 30 inches in diameter.

        - Anchors for [Standpipe] [Reservoirs]

          - The following requirements shall be met:

            - An adequate number of anchors designed to prevent overturning of the [standpipe] [reservoir] when empty shall be installed. If anchor bolts are used, the nominal diameter shall not be less than one inch, plus a corrosion allowance of at least 1/4 inch on the diameter. If anchor straps are used, they shall be pre-tensioned before welding to the tank shell.

            - The anchor bolts shall be a right angle bend, hook, or plate washer, while anchor straps shall have only a plate welded to the bottom. The anchors shall be inserted into the foundation to resist the computed uplift.

            - Attachment of anchors to the shell shall not add significant localized stresses to the shell. The method of attachment shall consider the effects of deflection and rotation of the tank shell. Anchors shall not be attached to the tank bottom. Attachment of the anchor bolts to the shell shall be through stiffened chair-type assemblies or anchor rings of adequate size and height.

      - CONCRETE WORK

        - Concrete work shall conform to Section [03 31 00.00 10 CAST-IN-PLACE 
STRUCTURAL CONCRETE][03 30 00 CAST-IN-PLACE CONCRETE].

      - CHLORINE

        - AWWA B300 for hypochlorites or AWWA B301 for liquid chlorine, mixed with water to give the solutions required in AWWA C652.

- EXECUTION

      - FOUNDATIONS

        - Foundations for the [standpipe] [reservoir] [tank columns and riser] and for the valve chamber shall be constructed of concrete, reinforced where necessary, and designed in accordance with Section 12 of AWWA D100 or Sections 11 and 8.5 of AWWA D103 for earth with a bearing value of [_____] psf, at elevation [_____], and constructed in conformance with the applicable requirements of Section [03 31 00.00 10 CAST-IN-PLACE STRUCTURAL CONCRETE][03 30 00 CAST-IN-PLACE CONCRETE], except as shown or specified herein. An AWWA D100 Type 1 or an AWWA D103 Type 1 or Type 2 foundation shall be provided for the [standpipe] [reservoir]. Factor of safety on overturning of [elevated tanks] [standpipe] [reservoir] under design windload shall be 1.33 minimum. When a footing is required, an inverted truncated pyramid of earth with 2 on 1 side slopes above top of footing maybe used in determining overturning stability.

      - EXCAVATING, FILLING, AND GRADING

        - Excavating, filling, and grading shall conform to the applicable
requirements of Section 31 00 00 EARTHWORK.

      - CATHODIC PROTECTION

        - Cathodic protection shall be provided, conforming to Section 26 42 15.00 10 CATHODIC PROTECTION SYSTEM (STEEL WATER TANKS).

      - OBSTRUCTION LIGHTING

        - Obstruction lighting shall be provided and installed as shown, and shall conform to Section 26 20 00 INTERIOR DISTRIBUTION SYSTEM or FAA AC 150/5345-43.

      - BEACON

        - Beacon shall be provided and installed as shown, and shall conform to
Section 26 20 00 INTERIOR DISTRIBUTION SYSTEM.

      - TANK INSTALLATION

        - Tank installation shall be in accordance with the following requirements:

          - Welding Section 8 of AWWA D100 or Section 6 of AWWA D103.

          - Erection Section 10 of AWWA D100 or Section 8 of AWWA D103.

      - INSPECTIONS AND TESTING

        - Tank inspection and testing shall be in accordance with Section 11 of AWWA D100 or Section 9 of AWWA D103. Mill and shop inspections [are not required] [are required and shall be performed by an approved commercial inspection agency].

        - Perform the radiographic inspections of the welded tank shell, the hydrostatic test and the vacuum box leak test of the tank bottom. Final hydrostatic and leak tests shall be performed before painting of welded tanks.

      - PIPING INSTALLATION (EXCEPT FOR OVERFLOW PIPING)

        - General Guidelines

          - Where details of fabrication or installation are not shown on the drawings, installation shall conform to Section 1 and 3 of AWWA C600.

        - Testing of Valves and Piping

          - After the [elevated tank] [standpipe] [reservoir] has been erected and the valves and piping installed, and before field painting is begun, the valves and piping shall be hydrostatically tested in accordance with Section 4 of AWWA C600. Replace with sound material any defective material disclosed by the pressure test; the test shall be repeated until the test results are satisfactory.

        - Polyethylene Encasement of Underground Ductile-Iron Piping Polyethylene encasement of underground ductile-iron piping shall be provided in addition to asphaltic coating in accordance with AWWA C105/A21.5.

        - Plugging Ends: Pipe ends left for future connections shall be capped or plugged as
directed.

      - PAINTING AND COATING OF TANK

        - Each coating manufacturer's technical data, application instructions, Material Safety Data Sheets (MSDS), and certificate for compliance for VOC content shall be submitted to the COTR. Application, curing time, mixing and thinning of the coating materials shall be in strict accordance with the manufacturers instructions. The use of thinners shall not alter the required minimum dry thickness or adversely affect the VOC content.

        - Exterior Surfaces (Welded Tanks)

          - [A prime coat, minimum of 2.0 mil thick followed by two coats of alkyd enamel, each a minimum of 1.5 mil thick shall be applied. The prime coat shall be rust inhibitive red iron oxide, zinc oxide, oil and alkyd primer without lead or chromate pigments, in accordance with SSPC Paint 25. The finish coats shall be [white alkyd enamel in accordance with Type I of SSPC Paint 104] [[_____] gloss alkyd enamel in accordance with SSPC Paint 21 ] [alternating panels (checkerboard) of white alkyd enamel in accordance with Type I of SSPC Paint 104 and international orange gloss alkyd enamel in accordance with SSPC Paint 21 color 12197].]

          - [[A gray vinyl prime coat a minimum of 1.5 mil thick followed by two coats of [white] [light gray] vinyl paint, each a minimum of 1.5 mil thick shall be applied.  SSPC PS 4.04] [A two-component catalyzed epoxy prime and intermediate coat,  The primer and paint shall be VR-3 in accordance with each a minimum of 3.0 mil thick, followed by a two-component catalyzed aliphatic polyurethane finish coat, a minimum of 1.5 mil thick, conforming to Type V of SSPC PS Guide 17.00 shall be applied. The prime coat shall be a green primer, Formula 150 in accordance with MIL-DTL-24441. The intermediate coat shall be white Formula 152 in accordance with MIL-DTL-24441 and may be tinted with pigment color. The finish coat shall be [white] [_____] [alternating panels (checkerboard) of international orange and white]].]

        - Interior Surfaces (Welded Tanks)

          - [A prime coat at least 3.0 mil thick and a [white] [_____] final coat at least 5.0 mil thick shall be applied. Each coat shall be a two-component catalyzed epoxy in accordance with MIL-PRF-23236. The primer shall contrast with the color of the finish coat.] [Four coats, each at least 1.5 mil thick, of VR-3 vinyl resin paint in accordance with SSPC PS 4.04 shall be applied. The second, third, and fourth coats shall be of contrasting colors.]

        - Bolted Tanks

          - The tanks shall have a coating applied to both the interior and exterior
surfaces in accordance with Section 10 of AWWA D103. Color shall be [as 
indicated on the drawings] [as approved] [_____].

      - DISINFECTION

        - The [elevated tank] [standpipe] [reservoir] and connecting lines thereto shall be disinfected with chlorine before being placed in operation.

        - Tank

          - The [elevated tank] [standpipe] [reservoir] shall be disinfected in accordance with [AWWA C652] [_____]. After the chlorination procedure Is completed and before the storage facility is placed in service, the COTR will collect samples of water in properly sterilized containers for bacteriological testing from the full facility in accordance with Section 7 of AWWA C652. The tank will not be accepted until satisfactory bacteriological results have been obtained.[ After coating system has been inspected, approved, and cured, rinse tank with potable water. Disinfect tank and connecting lines in accordance with AWWA C652,[Method 1] [Method 2] [or] [Method 3].]

        - Piping

          - The valves and piping shall be disinfected in accordance with Section 33 11 00 WATER DISTRIBUTION.

      - INSPECTION AND REPAIR

        - Prior to tank repair job, perform a detailed inspection of the structure and submit report by a certified inspector.

END OF SECTION 331615